## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-07-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.06 | NIS | 0.071 | 0.07 | NIS | NIS | 0.07
2 | 0.07 | 0.06 | 0.054 | 0.073 | NIS | 0.06 | 0.07
3 | 0.08 | 0.07 | 0.068 | 0.078 | 0.07 | 0.07 | 0.08
4 | 0.07 | NIS | 0.077 | 0.07 | 0.06 | 0.07 | 0.08
5 | 0.07 | NIS | 0.08 | NIS | NIS | NIS | 0.08
6 | 0.09 | 0.07 | 0.07 | 0.06 | 0.07 | 0.07 | 0.09
7 | 0.06 | 0.07 | NIS | NIS | NIS | 0.07 | 0.1
8 | 0.07 | 0.07 | 0.07 | NIS | 0.07 | 0.07 | 0.1
9 | 0.07 | 0.07 | 0.07 | 0.07 | NIS | NIS | 0.1
10 | NIS | 0.07 | 0.07 | 0.059 | 0.075 | 0.07 | 0.08
11 | 0.07 | 0.06 | 0.06 | NIS | NIS | NIS | 0.1
12 | 0.07 | 0.06 | 0.06 | 0.06 | 0.06 | NIS | 0.1
13 | 0.07 | 0.06 | NIS | NIS | 0.065 | 0.068 | 0.1
14 | 0.06 | 0.06 | 0.058 | 0.06 | NIS | 0.07 | 0.1
15 | NIS | NIS | 0.07 | 0.06 | 0.06 | 0.08 | 0.1
16 | 0.07 | 0.08 | 0.065 | NIS | NIS | NIS | 0.1
17 | NIS | 0.06 | 0.06 | 0.059 | 0.067 | NIS | 0.1
18 | 0.08 | 0.07 | 0.056 | 0.06 | 0.07 | 0.07 | 0.1
19 | 0.07 | 0.06 | NIS | NIS | NIS | 0.06 | 0.1
20 | 0.06 | 0.06 | 0.053 | 0.061 | 0.06 | 0.06 | 0.1
21 | 0.06 | 0.06 | NIS | NIS | NIS | NIS | 0.1
22 | 0.06 | 0.06 | 0.05 | 0.05 | 0.059 | 0.06 | 0.1
23 | 0.06 | NIS | 0.051 | 0.056 | NIS | NIS | 0.1
24 | NIS | 0.05 | 0.05 | 0.052 | 0.055 | 0.054 | 0.1
25 | NIS | NIS | 0.049 | NIS | NIS | 0.05 | 0.1
26 | 0.06 | 0.072 | 0.048 | 0.046 | NIS | 0.05 | 0.1
27 | 0.06 | 0.06 | 0.06 | NIS | NIS | NIS | 0.1
28 | NIS | NIS | 0.059 | 0.05 | 0.06 | 0.06 | 0.1
29 | 0.06 | 0.05 | 0.08 | NIS | 0.08 | NIS | 0.1
30 | NIS | 0.05 | 0.06 | 0.062 | 0.059 | NIS | 0.1
31 | NIS | NIS | 0.08 | 0.061 | 0.07 | NIS | 0.1
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:8/5//2024
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.12 | 63 | 70.56 | 24.1 | 8.7 | 14.126 | YES | 300
2 | 1.06 | 63 | 66.78 | 24 | 8.6 | 13.6084 | YES | 300
3 | 1.08 | 63 | 68.04 | 24.2 | 9 | 15.6122 | YES | 300
4 | 1.07 | 63 | 67.41 | 24.3 | 9 | 15.4907 | YES | 300
5 | 1.03 | 63 | 64.89 | 24.4 | 9 | 15.3177 | YES | 300
6 | 1.04 | 63 | 65.52 | 24.4 | 8.7 | 13.7193 | YES | 300
7 | 0.79 | 63 | 49.77 | 24.7 | 8.1 | 10.443 | YES | 300
8 | 1.1 | 63 | 69.3 | 25.2 | 8.8 | 13.5893 | YES | 300
9 | 1.08 | 63 | 68.04 | 25.8 | 8.7 | 12.5478 | YES | 300
10 | 1.02 | 63 | 64.26 | 26 | 8.8 | 12.7626 | YES | 300
11 | 1.18 | 63 | 74.34 | 25.9 | 8.4 | 11.2716 | YES | 300
12 | 1.19 | 63 | 74.97 | 25.7 | 8.1 | 10.2217 | YES | 300
13 | 1.12 | 63 | 70.56 | 26.1 | 8.2 | 10.2465 | YES | 300
14 | 1.23 | 63 | 77.49 | 25.9 | 8.2 | 10.5185 | YES | 300
15 | 1.27 | 63 | 80.01 | 25.8 | 7.9 | 9.5049 | YES | 300
16 | 1.14 | 63 | 71.82 | 25.7 | 8.3 | 10.9544 | YES | 300
17 | 0.9 | 63 | 56.7 | 25.7 | 8.2 | 10.2634 | YES | 300
18 | 1.09 | 63 | 68.67 | 25.8 | 8.3 | 10.8183 | YES | 300
19 | 1.2 | 63 | 75.6 | 25.5 | 7.9 | 9.6218 | YES | 300
20 | 1.07 | 63 | 67.41 | 25.6 | 8.2 | 10.5376 | YES | 300
21 | 1.11 | 63 | 69.93 | 25.7 | 8.1 | 10.1278 | YES | 300
22 | 0.95 | 63 | 59.85 | 24.2 | 8.1 | 11.0023 | YES | 300
23 | 0.93 | 63 | 58.59 | 23.5 | 8.4 | 12.8698 | YES | 300
24 | 0.83 | 63 | 52.29 | 23.5 | 8.9 | 15.3209 | YES | 300
25 | 0.95 | 63 | 59.85 | 24.4 | 9.2 | 16.3457 | YES | 300
26 | 1.06 | 63 | 66.78 | 24.1 | 8.8 | 14.5602 | YES | 300
27 | 1.13 | 63 | 71.19 | 23.7 | 8.3 | 12.5174 | YES | 300
28 | 0.84 | 63 | 52.92 | 24.2 | 8.6 | 13.0936 | YES | 300
29 | 1.15 | 63 | 72.45 | 24.1 | 8.2 | 11.7662 | YES | 300
30 | 0.96 | 63 | 60.48 | 24.3 | 8 | 10.5386 | YES | 300
31 | 1.09 | 63 | 68.67 | 24.3 | 8 | 10.6977 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2