## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-08-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.07 | 0.06 | 0.07 | 0.06 | NIS | NIS | 0.07
2 | 0.05 | 0.05 | 0.072 | 0.066 | NIS | NIS | 0.07
3 | NIS | 0.05 | 0.058 | NIS | 0.06 | 0.078 | 0.08
4 | NIS | NIS | 0.067 | 0.057 | 0.073 | 0.07 | 0.07
5 | 0.06 | 0.06 | NIS | 0.064 | 0.077 | NIS | 0.08
6 | NIS | 0.079 | 0.06 | 0.065 | 0.053 | NIS | 0.08
7 | 0.06 | 0.06 | 0.06 | NIS | 0.059 | 0.08 | 0.08
8 | 0.06 | 0.07 | 0.075 | 0.074 | NIS | NIS | 0.08
9 | NIS | 0.04 | 0.05 | 0.068 | NIS | NIS | 0.07
10 | NIS | NIS | 0.08 | 0.07 | 0.06 | 0.06 | 0.08
11 | 0.06 | 0.054 | 0.05 | NIS | NIS | NIS | 0.06
12 | NIS | 0.07 | 0.06 | 0.1 | 0.1 | NIS | 0.1
13 | 0.08 | 0.07 | NIS | NIS | 0.084 | 0.08 | 0.08
14 | 0.07 | 0.08 | 0.08 | 0.07 | NIS | NIS | 0.08
15 | 0.08 | 0.08 | 0.07 | 0.075 | 0.075 | NIS | 0.08
16 | NIS | NIS | 0.06 | 0.082 | 0.089 | NIS | 0.09
17 | 0.09 | 0.1 | 0.11 | NIS | 0.08 | 0.08 | 0.11
18 | 0.08 | NIS | 0.098 | NIS | NIS | 0.09 | 0.1
19 | 0.09 | 0.08 | NIS | NIS | 0.07 | 0.08 | 0.09
20 | NIS | NIS | NIS | 0.11 | 0.08 | 0.09 | 0.11
21 | 0.08 | 0.07 | 0.067 | NIS | NIS | NIS | 0.08
22 | NIS | NIS | 0.084 | 0.079 | NIS | 0.07 | 0.08
23 | 0.06 | 0.06 | NIS | NIS | 0.07 | NIS | 0.07
24 | NIS | NIS | NIS | 0.097 | 0.084 | 0.07 | 0.1
25 | NIS | NIS | NIS | 0.078 | NIS | NIS | 0.08
26 | NIS | 0.08 | 0.06 | 0.06 | 0.08 | 0.08 | 0.08
27 | NIS | NIS | 0.052 | 0.06 | NIS | NIS | 0.06
28 | NIS | NIS | 0.08 | 0.057 | 0.068 | 0.07 | 0.08
29 | 0.08 | NIS | 0.07 | 0.074 | NIS | NIS | 0.08
30 | NIS | 0.07 | 0.076 | 0.062 | NIS | NIS | 0.08
31 | NIS | NIS | 0.082 | 0.08 | 0.09 | 0.11 | 0.11
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:9/3/2024
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.12 | 63 | 70.56 | 24.8 | 8.6 | 12.9871 | YES | 300
2 | 1.03 | 63 | 64.89 | 24.9 | 8.6 | 12.768 | YES | 300
3 | 0.87 | 63 | 54.81 | 25.1 | 8.1 | 10.2588 | YES | 300
4 | 0.8 | 63 | 50.4 | 24.9 | 7.8 | 9.2141 | YES | 300
5 | 0.93 | 63 | 58.59 | 25 | 8.1 | 10.4001 | YES | 300
6 | 0.72 | 63 | 45.36 | 24.6 | 7.8 | 9.3168 | YES | 300
7 | 0.73 | 63 | 45.99 | 24.6 | 8.1 | 10.4412 | YES | 300
8 | 1.07 | 63 | 67.41 | 24.7 | 8.3 | 11.6236 | YES | 300
9 | 1.04 | 63 | 65.52 | 25 | 8 | 10.1449 | YES | 300
10 | 1.16 | 63 | 73.08 | 25.3 | 7.8 | 9.3494 | YES | 300
11 | 1.09 | 63 | 68.67 | 25.2 | 8.4 | 11.6938 | YES | 300
12 | 1.01 | 63 | 63.63 | 24.7 | 8 | 10.317 | YES | 300
13 | 0.96 | 63 | 60.48 | 24.7 | 8.2 | 11.0562 | YES | 300
14 | 0.83 | 63 | 52.29 | 24.1 | 8.6 | 13.1666 | YES | 300
15 | 1.05 | 63 | 66.15 | 24.4 | 8.5 | 12.7498 | YES | 300
16 | 0.87 | 63 | 54.81 | 24.2 | 8.2 | 11.3171 | YES | 300
17 | 1.08 | 63 | 68.04 | 24.2 | 8.2 | 11.5937 | YES | 300
18 | 0.62 | 63 | 39.06 | 23.6 | 8.1 | 11.0294 | YES | 300
19 | 1 | 63 | 63 | 23.6 | 8.5 | 13.3754 | YES | 300
20 | 0.69 | 63 | 43.47 | 24.3 | 7.6 | 8.7869 | YES | 300
21 | 1.08 | 63 | 68.04 | 23.3 | 8 | 11.4304 | YES | 300
22 | 0.92 | 63 | 57.96 | 23.3 | 7.8 | 10.4119 | YES | 300
23 | 0.86 | 63 | 54.18 | 23.3 | 7.6 | 9.5914 | YES | 300
24 | 0.61 | 63 | 38.43 | 22.3 | 7.7 | 10.3524 | YES | 300
25 | 0.66 | 63 | 41.58 | 22.3 | 7.6 | 10.0287 | YES | 300
26 | 0.88 | 63 | 55.44 | 22.4 | 7.8 | 11.0129 | YES | 300
27 | 0.72 | 63 | 45.36 | 22.5 | 7.2 | 8.5683 | YES | 300
28 | 0.68 | 63 | 42.84 | 22.4 | 6.9 | 7.6635 | YES | 300
29 | 1.12 | 63 | 70.56 | 21.8 | 7.7 | 11.3553 | YES | 300
30 | 1.03 | 63 | 64.89 | 21.7 | 7.7 | 11.3143 | YES | 300
31 | 0.81 | 63 | 51.03 | 22.2 | 7.3 | 9.1768 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2