## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-09-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.1 | NIS | 0.079 | NIS | NIS | NIS | 0.1
2 | 0.09 | 0.1 | 0.099 | 0.1 | NIS | NIS | 0.1
3 | NIS | NIS | NIS | 0.1 | 0.15 | NIS | 0.15
4 | NIS | 0.07 | 0.1 | 0.083 | 0.09 | NIS | 0.1
5 | NIS | 0.09 | 0.064 | 0.085 | 0.1 | NIS | 0.1
6 | NIS | 0.09 | 0.073 | 0.06 | NIS | NIS | 0.09
7 | NIS | NIS | 0.077 | 0.09 | 0.073 | NIS | 0.09
8 | NIS | NIS | NIS | 0.066 | 0.094 | 0.099 | 0.1
9 | NIS | 0.08 | 0.09 | NIS | NIS | 0.04 | 0.09
10 | 0.05 | 0.044 | 0.04 | 0.095 | 0.055 | NIS | 0.1
11 | NIS | 0.097 | 0.05 | 0.09 | NIS | 0.06 | 0.1
12 | NIS | NIS | NIS | NIS | 0.04 | NIS | 0.04
13 | NIS | 0.05 | NIS | 0.051 | NIS | NIS | 0.05
14 | NIS | NIS | 0.05 | 0.04 | NIS | NIS | 0.05
15 | NIS | NIS | 0.05 | NIS | 0.08 | NIS | 0.08
16 | NIS | 0.05 | 0.051 | 0.057 | NIS | NIS | 0.06
17 | NIS | 0.05 | 0.06 | 0.061 | NIS | NIS | 0.06
18 | NIS | 0.05 | 0.046 | 0.052 | NIS | NIS | 0.05
19 | NIS | 0.05 | 0.046 | 0.075 | NIS | NIS | 0.08
20 | NIS | NIS | 0.06 | 0.059 | 0.09 | NIS | 0.09
21 | NIS | NIS | 0.055 | 0.06 | 0.061 | NIS | 0.06
22 | NIS | NIS | 0.054 | NIS | NIS | NIS | 0.05
23 | NIS | 0.05 | 0.06 | 0.068 | NIS | NIS | 0.07
24 | NIS | 0.07 | 0.09 | 0.055 | NIS | NIS | 0.09
25 | NIS | 0.05 | 0.06 | 0.14 | NIS | NIS | 0.14
26 | NIS | 0.05 | 0.05 | 0.065 | NIS | NIS | 0.07
27 | NIS | 0.05 | 0.06 | 0.053 | 0.08 | NIS | 0.08
28 | NIS | NIS | 0.05 | NIS | NIS | NIS | 0.05
29 | NIS | NIS | 0.05 | 0.06 | 0.06 | NIS | 0.06
30 | NIS | 0.05 | 0.052 | 0.049 | NIS | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:10/7/2024
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.14 | 63 | 71.82 | 22.5 | 8.1 | 12.6071 | YES | 300
2 | 1.01 | 63 | 63.63 | 22.7 | 8.2 | 12.7204 | YES | 300
3 | 1.13 | 63 | 71.19 | 22.4 | 7.5 | 10.129 | YES | 300
4 | 1.07 | 63 | 67.41 | 22.5 | 7.7 | 10.7699 | YES | 300
5 | 1.03 | 63 | 64.89 | 22.2 | 7.6 | 10.5371 | YES | 300
6 | 1.03 | 63 | 64.89 | 22.8 | 7.8 | 10.9066 | YES | 300
7 | 1.01 | 63 | 63.63 | 23 | 7.9 | 11.1454 | YES | 300
8 | 0.74 | 63 | 46.62 | 22.9 | 7.8 | 10.4772 | YES | 300
9 | 0.95 | 63 | 59.85 | 22.9 | 7.3 | 8.8939 | YES | 300
10 | 0.88 | 63 | 55.44 | 23.2 | 8.1 | 11.6744 | YES | 300
11 | 0.9 | 63 | 56.7 | 23 | 7.4 | 9.1203 | YES | 300
12 | 0.98 | 63 | 61.74 | 22.6 | 7.8 | 10.9912 | YES | 300
13 | 0.84 | 63 | 52.92 | 21.9 | 7.2 | 9.0504 | YES | 300
14 | 1.02 | 63 | 64.26 | 22.1 | 7.2 | 9.1167 | YES | 300
15 | 0.99 | 63 | 62.37 | 22.1 | 7.6 | 10.5597 | YES | 300
16 | 0.71 | 63 | 44.73 | 21.3 | 7 | 8.6105 | YES | 300
17 | 1.05 | 63 | 66.15 | 21.1 | 7.5 | 10.9567 | YES | 300
18 | 1.1 | 63 | 69.3 | 21 | 7.4 | 10.6867 | YES | 300
19 | 1.03 | 63 | 64.89 | 20.7 | 7.3 | 10.4196 | YES | 300
20 | 1.17 | 63 | 73.71 | 20.8 | 7.5 | 11.3359 | YES | 300
21 | 1.19 | 63 | 74.97 | 20.3 | 7.5 | 11.7508 | YES | 300
22 | 1.06 | 63 | 66.78 | 20.6 | 8 | 13.6702 | YES | 300
23 | 1.07 | 63 | 67.41 | 20.2 | 7.8 | 13.0495 | YES | 300
24 | 1.14 | 63 | 71.82 | 20.5 | 7.8 | 12.8926 | YES | 300
25 | 1.14 | 63 | 71.82 | 20.7 | 7.5 | 11.3732 | YES | 300
26 | 1.12 | 63 | 70.56 | 20.4 | 7.4 | 11.1536 | YES | 300
27 | 1.06 | 63 | 66.78 | 20.3 | 7.4 | 11.1517 | YES | 300
28 | 1.32 | 63 | 83.16 | 20.2 | 7.4 | 11.5678 | YES | 300
29 | 1.24 | 63 | 78.12 | 19.9 | 7.2 | 10.8526 | YES | 300
30 | 1.18 | 63 | 74.34 | 19.4 | 7.3 | 11.5721 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2