## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-12-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.065 | 0.045 | 0.044 | 0.05 | 0.07
2 | 0.05 | NIS | 0.05 | NIS | NIS | NIS | 0.05
3 | NIS | 0.05 | 0.05 | 0.05 | NIS | NIS | 0.05
4 | NIS | 0.05 | 0.05 | 0.056 | NIS | NIS | 0.06
5 | NIS | NIS | 0.04 | 0.046 | NIS | NIS | 0.05
6 | NIS | NIS | 0.045 | 0.04 | NIS | NIS | 0.05
7 | NIS | NIS | 0.045 | 0.05 | 0.04 | NIS | 0.05
8 | NIS | NIS | 0.052 | 0.05 | 0.05 | NIS | 0.05
9 | NIS | 0.05 | 0.05 | 0.044 | NIS | NIS | 0.05
10 | NIS | 0.05 | 0.05 | 0.049 | 0.045 | NIS | 0.05
11 | NIS | 0.06 | 0.04 | 0.05 | NIS | NIS | 0.06
12 | NIS | 0.05 | 0.06 | 0.051 | 0.044 | NIS | 0.06
13 | NIS | NIS | 0.046 | 0.05 | NIS | NIS | 0.05
14 | NIS | 0.05 | 0.06 | 0.05 | 0.05 | NIS | 0.06
15 | NIS | NIS | 0.07 | 0.063 | NIS | NIS | 0.07
16 | NIS | 0.08 | 0.057 | 0.046 | NIS | NIS | 0.08
17 | NIS | 0.05 | 0.04 | 0.052 | NIS | NIS | 0.05
18 | NIS | 0.07 | 0.04 | 0.05 | NIS | NIS | 0.07
19 | NIS | 0.05 | 0.06 | 0.052 | 0.052 | NIS | 0.06
20 | NIS | NIS | 0.059 | 0.071 | 0.085 | NIS | 0.09
21 | NIS | NIS | 0.056 | NIS | NIS | NIS | 0.06
22 | 0.08 | 0.05 | 0.088 | 0.063 | 0.06 | NIS | 0.09
23 | NIS | 0.07 | 0.07 | NIS | NIS | NIS | 0.07
24 | 0.091 | 0.08 | 0.06 | 0.05 | NIS | NIS | 0.09
25 | NIS | NIS | 0.08 | 0.09 | 0.09 | NIS | 0.09
26 | NIS | 0.071 | 0.063 | 0.07 | NIS | NIS | 0.07
27 | NIS | 0.06 | 0.077 | 0.062 | NIS | NIS | 0.08
28 | NIS | 0.09 | 0.06 | 0.074 | NIS | NIS | 0.09
29 | 0.08 | 0.079 | NIS | NIS | NIS | NIS | 0.08
30 | NIS | NIS | 0.061 | 0.056 | NIS | NIS | 0.06
31 | NIS | 0.05 | 0.06 | 0.057 | NIS | NIS | 0.06
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:1/8/2025
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-12-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.16 | 63 | 73.08 | 8.7 | 6.7 | 19.2651 | YES | 300
2 | 1.33 | 63 | 83.79 | 8.8 | 6.7 | 19.5059 | YES | 300
3 | 1.24 | 63 | 78.12 | 8.4 | 6.7 | 19.8208 | YES | 300
4 | 1.18 | 63 | 74.34 | 8 | 6.7 | 20.2092 | YES | 300
5 | 1.25 | 63 | 78.75 | 8.1 | 6.7 | 20.2354 | YES | 300
6 | 1.29 | 63 | 81.27 | 8.4 | 6.7 | 19.9318 | YES | 300
7 | 1.29 | 63 | 81.27 | 8.7 | 7.4 | 25.0003 | YES | 300
8 | 1.25 | 63 | 78.75 | 8.4 | 6.7 | 19.843 | YES | 300
9 | 1.15 | 63 | 72.45 | 8.2 | 7.9 | 30.4461 | YES | 300
10 | 1.1 | 63 | 69.3 | 8.2 | 6.8 | 20.4697 | YES | 300
11 | 1.11 | 63 | 69.93 | 8.4 | 6.9 | 20.9446 | YES | 300
12 | 1.04 | 63 | 65.52 | 7.9 | 6.7 | 20.0256 | YES | 300
13 | 1.19 | 63 | 74.97 | 8.9 | 6.4 | 17.2118 | YES | 300
14 | 1.13 | 63 | 71.19 | 8.2 | 6.7 | 19.8359 | YES | 300
15 | 1.09 | 63 | 68.67 | 8.1 | 6.6 | 19.1992 | YES | 300
16 | 1.03 | 63 | 64.89 | 8 | 7.8 | 29.3544 | YES | 300
17 | 1.06 | 63 | 66.78 | 8.8 | 7.4 | 24.1901 | YES | 300
18 | 1.2 | 63 | 75.6 | 9.7 | 7.5 | 23.9858 | YES | 300
19 | 1 | 63 | 63 | 9 | 7.5 | 24.564 | YES | 300
20 | 1.02 | 63 | 64.26 | 8.8 | 7.3 | 23.2421 | YES | 300
21 | 1.05 | 63 | 66.15 | 8.9 | 7.3 | 23.1673 | YES | 300
22 | 1.15 | 63 | 72.45 | 11 | 7 | 18.3889 | YES | 300
23 | 0.97 | 63 | 61.11 | 8.7 | 7.1 | 21.6816 | YES | 300
24 | 0.99 | 63 | 62.37 | 9.1 | 7 | 20.4395 | YES | 300
25 | 1.22 | 63 | 76.86 | 9.2 | 6.9 | 20.1225 | YES | 300
26 | 1.18 | 63 | 74.34 | 8.9 | 7 | 21.1557 | YES | 300
27 | 0.95 | 63 | 59.85 | 8.7 | 7.3 | 23.2115 | YES | 300
28 | 0.99 | 63 | 62.37 | 9.7 | 6.9 | 18.9853 | YES | 300
29 | 0.95 | 63 | 59.85 | 9.9 | 6.8 | 18.027 | YES | 300
30 | 1.05 | 63 | 66.15 | 10.2 | 6.7 | 17.2769 | YES | 300
31 | 1.04 | 63 | 65.52 | 8.9 | 7.1 | 21.5675 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2