## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-01-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | 0.05 | 0.06 | 0.05 | NIS | NIS | 0.06
2 | NIS | 0.07 | 0.052 | 0.085 | NIS | NIS | 0.09
3 | NIS | 0.06 | 0.065 | 0.095 | NIS | NIS | 0.1
4 | NIS | 0.07 | 0.077 | 0.08 | 0.08 | NIS | 0.08
5 | NIS | NIS | 0.075 | 0.07 | 0.06 | NIS | 0.08
6 | NIS | 0.07 | 0.12 | 0.044 | NIS | NIS | 0.12
7 | NIS | 0.06 | 0.05 | 0.055 | NIS | NIS | 0.06
8 | NIS | 0.05 | NIS | 0.05 | NIS | NIS | 0.05
9 | NIS | 0.07 | 0.056 | 0.05 | NIS | NIS | 0.07
10 | NIS | 0.06 | 0.05 | 0.065 | NIS | NIS | 0.07
11 | NIS | NIS | 0.09 | 0.05 | 0.055 | 0.07 | 0.09
12 | NIS | NIS | NIS | 0.045 | NIS | NIS | 0.05
13 | NIS | 0.06 | 0.05 | 0.043 | 0.05 | NIS | 0.06
14 | NIS | 0.05 | 0.056 | 0.051 | 0.062 | NIS | 0.06
15 | NIS | 0.07 | 0.048 | 0.05 | NIS | NIS | 0.07
16 | NIS | 0.05 | 0.054 | 0.04 | NIS | NIS | 0.05
17 | NIS | 0.05 | 0.046 | 0.05 | NIS | NIS | 0.05
18 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
19 | NIS | 0.08 | 0.05 | 0.06 | NIS | NIS | 0.08
20 | NIS | 0.05 | 0.05 | 0.05 | NIS | NIS | 0.05
21 | NIS | 0.05 | 0.07 | 0.075 | NIS | NIS | 0.08
22 | NIS | 0.05 | 0.05 | 0.055 | NIS | NIS | 0.06
23 | NIS | 0.05 | 0.078 | 0.08 | 0.055 | NIS | 0.08
24 | NIS | NIS | 0.055 | 0.085 | 0.08 | NIS | 0.09
25 | NIS | NIS | NIS | 0.06 | 0.05 | 0.05 | 0.06
26 | 0.06 | NIS | 0.08 | 0.08 | NIS | NIS | 0.08
27 | NIS | NIS | NIS | NIS | 0.084 | 0.07 | 0.08
28 | 0.08 | NIS | 0.062 | 0.046 | 0.053 | NIS | 0.08
29 | NIS | 0.04 | 0.09 | 0.072 | 0.055 | NIS | 0.09
30 | NIS | 0.05 | 0.045 | 0.097 | NIS | NIS | 0.1
31 | NIS | 0.09 | 0.072 | 0.082 | NIS | NIS | 0.09
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-02-03
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.95 | 63 | 59.85 | 8.8 | 7.1 | 21.4908 | YES | 300
2 | 1.03 | 63 | 64.89 | 9.9 | 7.2 | 20.892 | YES | 300
3 | 0.98 | 63 | 61.74 | 9.8 | 7.5 | 23.2379 | YES | 300
4 | 0.97 | 63 | 61.11 | 8.6 | 7.3 | 23.4192 | YES | 300
5 | 1.05 | 63 | 66.15 | 9.4 | 7.5 | 24.0548 | YES | 300
6 | 1.04 | 63 | 65.52 | 9.2 | 7.7 | 26.1482 | YES | 300
7 | 1.01 | 63 | 63.63 | 9.3 | 7.6 | 24.9774 | YES | 300
8 | 1.09 | 63 | 68.67 | 10.1 | 7.8 | 25.6594 | YES | 300
9 | 1.09 | 63 | 68.67 | 10.3 | 7.8 | 25.3182 | YES | 300
10 | 0.98 | 63 | 61.74 | 9.8 | 7.6 | 24.0756 | YES | 300
11 | 1.07 | 63 | 67.41 | 10 | 7.4 | 22.3642 | YES | 300
12 | 1.1 | 63 | 69.3 | 10.1 | 7.6 | 23.9246 | YES | 300
13 | 1.12 | 63 | 70.56 | 8.9 | 7.5 | 25.0702 | YES | 300
14 | 1.21 | 63 | 76.23 | 8.9 | 7.6 | 26.2505 | YES | 300
15 | 1.13 | 63 | 71.19 | 9.3 | 7.6 | 25.3228 | YES | 300
16 | 1.13 | 63 | 71.19 | 8.5 | 7.7 | 27.6941 | YES | 300
17 | 1.13 | 63 | 71.19 | 8.1 | 7.7 | 28.4519 | YES | 300
18 | 1.13 | 63 | 71.19 | 8.1 | 7.7 | 28.4519 | YES | 300
19 | 1.21 | 63 | 76.23 | 7.9 | 7.8 | 30.1782 | YES | 300
20 | 1.15 | 63 | 72.45 | 7.5 | 7.9 | 31.9312 | YES | 300
21 | 1.23 | 63 | 77.49 | 7.3 | 7.3 | 26.3133 | YES | 300
22 | 1.22 | 63 | 76.86 | 6.8 | 7.6 | 30.2837 | YES | 300
23 | 1.15 | 63 | 72.45 | 9.5 | 7.4 | 23.3278 | YES | 300
24 | 1.14 | 63 | 71.82 | 10 | 7.2 | 21.0135 | YES | 300
25 | 1.23 | 63 | 77.49 | 7.8 | 7.1 | 23.7001 | YES | 300
26 | 1.16 | 63 | 73.08 | 8.4 | 7.1 | 22.5953 | YES | 300
27 | 1.26 | 63 | 79.38 | 9.4 | 7.6 | 25.5315 | YES | 300
28 | 1.26 | 63 | 79.38 | 6.5 | 8.2 | 38.6575 | YES | 300
29 | 1.23 | 63 | 77.49 | 5.9 | 8.4 | 43.2276 | YES | 300
30 | 1.26 | 63 | 79.38 | 6.8 | 8.1 | 36.5022 | YES | 300
31 | 1.22 | 63 | 76.86 | 7.1 | 8.2 | 36.9173 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2