## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-03-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.07 | 0.09 | 0.12 | 0.1 | NIS | NIS | 0.12
2 | NIS | 0.1 | NIS | 0.06 | NIS | NIS | 0.1
3 | NIS | NIS | 0.07 | 0.09 | 0.13 | 0.14 | 0.14
4 | 0.08 | 0.14 | 0.07 | 0.17 | 0.1 | NIS | 0.17
5 | NIS | NIS | 0.13 | NIS | 0.109 | NIS | 0.13
6 | NIS | NIS | 0.16 | 0.099 | NIS | NIS | 0.16
7 | NIS | NIS | 0.05 | 0.056 | 0.051 | 0.06 | 0.06
8 | 0.05 | 0.07 | 0.054 | NIS | NIS | NIS | 0.07
9 | NIS | NIS | 0.059 | 0.06 | 0.06 | 0.06 | 0.06
10 | NIS | 0.06 | 0.074 | 0.07 | 0.085 | NIS | 0.09
11 | NIS | 0.06 | 0.067 | NIS | NIS | NIS | 0.07
12 | NIS | 0.12 | 0.062 | 0.18 | NIS | NIS | 0.18
13 | NIS | NIS | NIS | 0.139 | NIS | NIS | 0.14
14 | NIS | NIS | 0.077 | 0.069 | 0.128 | NIS | 0.13
15 | 0.06 | 0.05 | NIS | 0.045 | NIS | NIS | 0.06
16 | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
17 | NIS | NIS | 0.049 | 0.046 | 0.046 | NIS | 0.05
18 | NIS | NIS | 0.049 | 0.095 | 0.047 | NIS | 0.1
19 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
20 | NIS | 0.05 | 0.046 | 0.05 | NIS | NIS | 0.05
21 | NIS | 0.05 | 0.05 | 0.048 | 0.05 | NIS | 0.05
22 | NIS | 0.06 | 0.05 | 0.05 | NIS | NIS | 0.06
23 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
24 | NIS | 0.05 | 0.05 | 0.053 | NIS | NIS | 0.05
25 | NIS | 0.06 | 0.06 | 0.05 | 0.07 | NIS | 0.07
26 | NIS | NIS | 0.066 | NIS | 0.088 | NIS | 0.09
27 | NIS | NIS | 0.078 | 0.118 | 0.095 | NIS | 0.12
28 | NIS | NIS | 0.069 | 0.085 | NIS | NIS | 0.09
29 | NIS | NIS | 0.07 | 0.085 | 0.08 | 0.09 | 0.09
30 | NIS | NIS | 0.08 | 0.06 | 0.07 | 0.09 | 0.09
31 | 0.07 | NIS | NIS | 0.055 | 0.06 | NIS | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 4/1/2025
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.22 | 63 | 76.86 | 9.5 | 8 | 29.1387 | YES | 300
2 | 1.12 | 63 | 70.56 | 10.4 | 8 | 27.1063 | YES | 300
3 | 1.14 | 63 | 71.82 | 11.2 | 7.9 | 24.8463 | YES | 300
4 | 1.11 | 63 | 69.93 | 9.8 | 8.3 | 31.4199 | YES | 300
5 | 1.07 | 63 | 67.41 | 10.7 | 8.2 | 28.3782 | YES | 300
6 | 1.23 | 63 | 77.49 | 10.6 | 8.3 | 30.1754 | YES | 300
7 | 1.16 | 63 | 73.08 | 10.9 | 8.5 | 31.53 | YES | 300
8 | 0.96 | 63 | 60.48 | 11.3 | 8.6 | 31.0834 | YES | 300
9 | 1.02 | 63 | 64.26 | 11.2 | 8.3 | 28.2773 | YES | 300
10 | 0.91 | 63 | 57.33 | 11.7 | 8.5 | 29.008 | YES | 300
11 | 0.88 | 63 | 55.44 | 12.4 | 8.5 | 27.5729 | YES | 300
12 | 1 | 63 | 63 | 12.2 | 8.2 | 25.4497 | YES | 300
13 | 1.22 | 63 | 76.86 | 12.2 | 8.5 | 29.0686 | YES | 300
14 | 1.15 | 63 | 72.45 | 12.2 | 8.1 | 24.9842 | YES | 300
15 | 1.09 | 63 | 68.67 | 12 | 8.2 | 26.0606 | YES | 300
16 | 0.96 | 63 | 60.48 | 11.8 | 7.7 | 21.7964 | YES | 300
17 | 1.1 | 63 | 69.3 | 10.9 | 8 | 26.1506 | YES | 300
18 | 1.05 | 63 | 66.15 | 11 | 8 | 25.8271 | YES | 300
19 | 1.13 | 63 | 71.19 | 11 | 8.2 | 28.0028 | YES | 300
20 | 1 | 63 | 63 | 11.4 | 7.8 | 23.2886 | YES | 300
21 | 0.94 | 63 | 59.22 | 11.1 | 8 | 25.3333 | YES | 300
22 | 1.08 | 63 | 68.04 | 11.5 | 7.8 | 23.3459 | YES | 300
23 | 1.14 | 63 | 71.82 | 11.9 | 7.8 | 22.8902 | YES | 300
24 | 1.05 | 63 | 66.15 | 11.8 | 8.3 | 27.2504 | YES | 300
25 | 1.07 | 63 | 67.41 | 11.5 | 8.3 | 27.8711 | YES | 300
26 | 1.12 | 63 | 70.56 | 12.4 | 8.2 | 25.459 | YES | 300
27 | 1.17 | 63 | 73.71 | 12.6 | 8.9 | 32.7652 | YES | 300
28 | 1.18 | 63 | 74.34 | 13.2 | 8.4 | 26.257 | YES | 300
29 | 1.16 | 63 | 73.08 | 12.6 | 8.3 | 26.2751 | YES | 300
30 | 0.96 | 63 | 60.48 | 12.9 | 8 | 22.5584 | YES | 300
31 | 1.17 | 63 | 73.71 | 13.4 | 7.9 | 21.5414 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2