## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-04-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.06 | 0.065 | 0.059 | NIS | 0.07
2 | NIS | NIS | 0.057 | 0.057 | 0.064 | NIS | 0.06
3 | NIS | NIS | 0.06 | 0.07 | 0.07 | NIS | 0.07
4 | NIS | NIS | 0.065 | 0.066 | 0.07 | NIS | 0.07
5 | NIS | NIS | NIS | 0.078 | 0.071 | 0.093 | 0.09
6 | NIS | NIS | NIS | 0.079 | 0.07 | NIS | 0.08
7 | NIS | NIS | 0.066 | 0.105 | 0.07 | NIS | 0.11
8 | NIS | NIS | 0.081 | 0.07 | 0.071 | NIS | 0.08
9 | NIS | NIS | 0.082 | 0.078 | 0.086 | 0.09 | 0.09
10 | NIS | NIS | 0.08 | 0.066 | NIS | NIS | 0.08
11 | NIS | NIS | 0.08 | 0.089 | 0.07 | NIS | 0.09
12 | NIS | NIS | NIS | 0.067 | NIS | NIS | 0.07
13 | NIS | 0.06 | 0.07 | 0.07 | 0.069 | 0.08 | 0.08
14 | NIS | NIS | 0.06 | 0.079 | 0.062 | NIS | 0.08
15 | NIS | 0.06 | 0.06 | 0.11 | NIS | NIS | 0.11
16 | NIS | 0.06 | 0.087 | 0.058 | 0.065 | NIS | 0.09
17 | NIS | 0.05 | 0.06 | 0.06 | NIS | NIS | 0.06
18 | NIS | NIS | 0.052 | 0.052 | 0.08 | NIS | 0.08
19 | NIS | NIS | 0.055 | 0.06 | 0.06 | 0.07 | 0.07
20 | NIS | NIS | 0.057 | 0.08 | NIS | NIS | 0.08
21 | NIS | 0.09 | 0.09 | 0.08 | NIS | NIS | 0.09
22 | NIS | 0.05 | 0.06 | 0.07 | 0.08 | NIS | 0.08
23 | NIS | NIS | 0.054 | 0.05 | 0.06 | NIS | 0.06
24 | NIS | NIS | 0.051 | 0.05 | 0.051 | NIS | 0.05
25 | NIS | NIS | 0.06 | NIS | NIS | NIS | 0.06
26 | NIS | NIS | 0.1 | 0.047 | 0.058 | 0.05 | 0.1
27 | 0.05 | 0.05 | NIS | 0.045 | NIS | NIS | 0.05
28 | NIS | 0.05 | 0.052 | 0.05 | 0.047 | 0.06 | 0.06
29 | 0.06 | NIS | 0.06 | 0.059 | NIS | NIS | 0.06
30 | NIS | 0.05 | 0.044 | 0.051 | 0.06 | 0.06 | 0.06
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-05-01
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.19 | 63 | 74.97 | 13.1 | 7.9 | 22.0234 | YES | 300
2 | 1.15 | 63 | 72.45 | 13.4 | 7.9 | 21.4927 | YES | 300
3 | 0.97 | 63 | 61.11 | 13 | 8.3 | 25.0477 | YES | 300
4 | 1 | 63 | 63 | 13 | 8.4 | 26.0715 | YES | 300
5 | 1.02 | 63 | 64.26 | 13.3 | 8.3 | 24.6951 | YES | 300
6 | 1.17 | 63 | 73.71 | 13.7 | 8.5 | 26.3235 | YES | 300
7 | 1.12 | 63 | 70.56 | 14.1 | 8.4 | 24.5749 | YES | 300
8 | 1.15 | 63 | 72.45 | 13.9 | 8.5 | 25.9197 | YES | 300
9 | 1.16 | 63 | 73.08 | 14.1 | 8.5 | 25.6085 | YES | 300
10 | 1.14 | 63 | 71.82 | 14 | 8.6 | 26.6806 | YES | 300
11 | 1.17 | 63 | 73.71 | 14.2 | 8.3 | 23.6662 | YES | 300
12 | 1.17 | 63 | 73.71 | 14.7 | 8.1 | 21.2731 | YES | 300
13 | 0.91 | 63 | 57.33 | 14.6 | 7.7 | 17.9429 | YES | 300
14 | 1.09 | 63 | 68.67 | 15 | 7.9 | 19.1985 | YES | 300
15 | 1.02 | 63 | 64.26 | 14.8 | 8.2 | 21.5557 | YES | 300
16 | 0.98 | 63 | 61.74 | 15.1 | 8.2 | 21.0361 | YES | 300
17 | 1 | 63 | 63 | 15.5 | 8.3 | 21.3019 | YES | 300
18 | 0.91 | 63 | 57.33 | 15.3 | 8.4 | 22.1678 | YES | 300
19 | 1.09 | 63 | 68.67 | 15.6 | 8.4 | 22.1787 | YES | 300
20 | 1.09 | 63 | 68.67 | 16.1 | 8.3 | 20.6812 | YES | 300
21 | 0.89 | 63 | 56.07 | 16.3 | 7.9 | 17.2142 | YES | 300
22 | 0.96 | 63 | 60.48 | 16 | 7.7 | 16.4399 | YES | 300
23 | 1.04 | 63 | 65.52 | 16.1 | 8.3 | 20.5645 | YES | 300
24 | 0.98 | 63 | 61.74 | 16.1 | 8 | 18.2869 | YES | 300
25 | 1.07 | 63 | 67.41 | 16.6 | 7.7 | 15.9946 | YES | 300
26 | 0.86 | 63 | 54.18 | 16.3 | 7.8 | 16.5329 | YES | 300
27 | 1.09 | 63 | 68.67 | 16.4 | 7.8 | 16.8583 | YES | 300
28 | 1 | 63 | 63 | 16.4 | 7.8 | 16.6867 | YES | 300
29 | 1.14 | 63 | 71.82 | 16.4 | 7.9 | 17.5927 | YES | 300
30 | 1.01 | 63 | 63.63 | 16.7 | 8 | 17.6318 | YES | 300
31 |  | 63
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2