## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-05-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.058 | 0.055 | NIS | NIS | 0.06
2 | NIS | 0.06 | 0.05 | 0.06 | 0.06 | NIS | 0.06
3 | NIS | NIS | 0.07 | 0.07 | 0.1 | NIS | 0.1
4 | NIS | NIS | 0.07 | 0.06 | 0.05 | 0.05 | 0.07
5 | NIS | 0.05 | 0.06 | 0.06 | 0.06 | NIS | 0.06
6 | NIS | NIS | 0.07 | 0.07 | 0.06 | NIS | 0.07
7 | NIS | 0.05 | 0.05 | 0.05 | 0.05 | NIS | 0.05
8 | NIS | NIS | 0.04 | 0.04 | 0.05 | NIS | 0.05
9 | NIS | NIS | 0.04 | 0.04 | 0.07 | NIS | 0.07
10 | NIS | NIS | 0.05 | 0.05 | 0.08 | 0.07 | 0.08
11 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
12 | NIS | 0.04 | 0.05 | 0.08 | 0.09 | NIS | 0.09
13 | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.06 | 0.06
14 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
15 | NIS | 0.05 | 0.05 | 0.05 | 0.06 | NIS | 0.06
16 | NIS | NIS | NIS | 0.05 | 0.06 | 0.06 | 0.06
17 | NIS | NIS | NIS | 0.05 | 0.07 | 0.07 | 0.07
18 | NIS | NIS | NIS | 0.05 | 0.07 | 0.06 | 0.07
19 | 0.06 | NIS | 0.05 | NIS | NIS | NIS | 0.06
20 | NIS | 0.05 | 0.05 | 0.05 | 0.07 | 0.07 | 0.07
21 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
22 | NIS | NIS | 0.06 | 0.07 | 0.05 | NIS | 0.07
23 | NIS | 0.05 | 0.07 | 0.06 | 0.08 | NIS | 0.08
24 | NIS | 0.05 | NIS | 0.06 | 0.07 | 0.09 | 0.09
25 | 0.07 | 0.06 | NIS | 0.07 | NIS | NIS | 0.07
26 | NIS | 0.08 | 0.05 | 0.08 | 0.07 | 0.07 | 0.08
27 | NIS | NIS | 0.06 | 0.07 | 0.07 | NIS | 0.07
28 | NIS | 0.06 | 0.05 | 0.08 | 0.07 | NIS | 0.08
29 | NIS | 0.06 | 0.07 | 0.06 | 0.08 | NIS | 0.08
30 | NIS | 0.05 | 0.07 | 0.08 | 0.08 | 0.09 | 0.09
31 | NIS | NIS | 0.06 | 0.09 | 0.06 | NIS | 0.09
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-06-02
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.95 | 63 | 59.85 | 17 | 8.1 | 17.812 | YES | 300
2 | 1.04 | 63 | 65.52 | 17.2 | 8 | 17.1132 | YES | 300
3 | 1.13 | 63 | 71.19 | 17.4 | 7.9 | 16.4411 | YES | 300
4 | 1.07 | 63 | 67.41 | 17.3 | 8 | 17.0577 | YES | 300
5 | 1.04 | 63 | 65.52 | 17.5 | 8 | 16.7748 | YES | 300
6 | 1.02 | 63 | 64.26 | 17.8 | 7.8 | 15.2345 | YES | 300
7 | 1.09 | 63 | 68.67 | 18 | 8.1 | 16.9327 | YES | 300
8 | 1.07 | 63 | 67.41 | 18.3 | 7.8 | 14.8185 | YES | 300
9 | 1.06 | 63 | 66.78 | 18.3 | 8.2 | 17.1644 | YES | 300
10 | 1.07 | 63 | 67.41 | 18.8 | 8.1 | 16.0176 | YES | 300
11 | 1.09 | 63 | 68.67 | 19 | 8.3 | 17.0581 | YES | 300
12 | 0.95 | 63 | 59.85 | 18.6 | 7.7 | 13.8044 | YES | 300
13 | 1.08 | 63 | 68.04 | 18.5 | 7.7 | 14.105 | YES | 300
14 | 1.15 | 63 | 72.45 | 18.5 | 8.1 | 16.4904 | YES | 300
15 | 1.06 | 63 | 66.78 | 18.5 | 8 | 15.7292 | YES | 300
16 | 1.1 | 63 | 69.3 | 18.6 | 8.1 | 16.288 | YES | 300
17 | 1.05 | 63 | 66.15 | 18.4 | 8.1 | 16.4128 | YES | 300
18 | 0.91 | 63 | 57.33 | 18.5 | 8.2 | 16.651 | YES | 300
19 | 1.13 | 63 | 71.19 | 18.4 | 8.2 | 17.1867 | YES | 300
20 | 0.98 | 63 | 61.74 | 18.5 | 7.8 | 14.4724 | YES | 300
21 | 1.1 | 63 | 69.3 | 18.5 | 8.2 | 17.0146 | YES | 300
22 | 1.1 | 63 | 69.3 | 18.4 | 8.2 | 17.1282 | YES | 300
23 | 1.02 | 63 | 64.26 | 18.5 | 8.2 | 16.8606 | YES | 300
24 | 0.98 | 63 | 61.74 | 18.6 | 8.2 | 16.6727 | YES | 300
25 | 1.21 | 63 | 76.23 | 19.1 | 8.1 | 15.9526 | YES | 300
26 | 0.98 | 63 | 61.74 | 19.2 | 7.8 | 13.8106 | YES | 300
27 | 1.15 | 63 | 72.45 | 19.2 | 8.5 | 18.2471 | YES | 300
28 | 0.96 | 63 | 60.48 | 19.8 | 8.5 | 17.1591 | YES | 300
29 | 0.89 | 63 | 56.07 | 20.2 | 8 | 13.7709 | YES | 300
30 | 1.01 | 63 | 63.63 | 20.7 | 8.5 | 16.2531 | YES | 300
31 | 1 | 63 | 63 | 21.2 | 8.5 | 15.7025 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2