## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-07-25
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.04 | 0.04 | NIS | NIS | NIS | NIS | 0.04
2 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06 | 0.06
3 | 0.05 | 0.04 | NIS | 0.04 | 0.05 | 0.06 | 0.06
4 | 0.04 | NIS | 0.04 | 0.04 | 0.05 | NIS | 0.05
5 | NIS | 0.09 | 0.04 | 0.05 | 0.05 | 0.05 | 0.09
6 | 0.05 | 0.05 | 0.04 | 0.05 | 0.06 | 0.05 | 0.06
7 | 0.05 | 0.05 | 0.04 | 0.05 | 0.05 | 0.06 | 0.06
8 | 0.11 | 0.05 | 0.04 | 0.05 | 0.06 | 0.06 | 0.11
9 | 0.05 | NIS | 0.04 | 0.06 | 0.05 | NIS | 0.06
10 | NIS | 0.05 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05
11 | 0.05 | 0.06 | 0.04 | 0.05 | 0.06 | NIS | 0.06
12 | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.06 | 0.06
13 | 0.05 | 0.05 | 0.05 | 0.05 | NIS | NIS | 0.05
14 | NIS | 0.05 | 0.05 | NIS | 0.05 | 0.06 | 0.06
15 | 0.05 | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
16 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
17 | 0.05 | 0.05 | NIS | NIS | NIS | 0.05 | 0.05
18 | 0.1 | 0.05 | 0.05 | NIS | NIS | NIS | 0.1
19 | 0.05 | NIS | 0.09 | 0.05 | 0.06 | 0.07 | 0.09
20 | 0.06 | 0.1 | 0.06 | 0.06 | NIS | NIS | 0.1
21 | NIS | 0.05 | 0.05 | 0.05 | 0.07 | 0.07 | 0.07
22 | NIS | 0.09 | 0.05 | 0.08 | 0.08 | 0.08 | 0.09
23 | NIS | 0.07 | 0.07 | 0.07 | 0.09 | 0.08 | 0.09
24 | 0.09 | 0.08 | NIS | 0.07 | 0.08 | NIS | 0.09
25 | 0.07 | 0.1 | 0.07 | 0.1 | 0.09 | NIS | 0.1
26 | NIS | 0.09 | 0.07 | 0.07 | 0.1 | 0.1 | 0.1
27 | NIS | 0.1 | 0.09 | 0.08 | 0.11 | 0.09 | 0.11
28 | NIS | 0.08 | 0.11 | 0.08 | 0.11 | 0.1 | 0.11
29 | NIS | NIS | 0.07 | 0.09 | 0.1 | 0.12 | 0.12
30 | 0.09 | 0.08 | NIS | NIS | 0.1 | 0.09 | 0.1
31 | NIS | 0.09 | 0.12 | 0.1 | 0.11 | NIS | 0.12
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-08-12
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-07-25 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.15 | 63 | 72.45 | 24.4 | 9.2 | 16.7218 | YES | 300
2 | 1.01 | 63 | 63.63 | 24.4 | 9 | 15.2829 | YES | 300
3 | 1.03 | 63 | 64.89 | 24.7 | 9.2 | 16.1687 | YES | 300
4 | 1.06 | 63 | 66.78 | 24.6 | 9.2 | 16.3325 | YES | 300
5 | 0.8 | 63 | 50.4 | 23.3 | 8.9 | 15.4737 | YES | 300
6 | 1.1 | 63 | 69.3 | 23.8 | 9 | 16.0707 | YES | 300
7 | 1.14 | 63 | 71.82 | 23.9 | 9.2 | 17.268 | YES | 300
8 | 1.1 | 63 | 69.3 | 24.6 | 9.1 | 15.8108 | YES | 300
9 | 1.1 | 63 | 69.3 | 24.8 | 9.3 | 16.7999 | YES | 300
10 | 0.75 | 63 | 47.25 | 25.1 | 9.1 | 14.6939 | YES | 300
11 | 1.1 | 63 | 69.3 | 24.9 | 9.3 | 16.6884 | YES | 300
12 | 0.96 | 63 | 60.48 | 25.1 | 8.8 | 13.4634 | YES | 300
13 | 1.1 | 63 | 69.3 | 25.6 | 9 | 14.2512 | YES | 300
14 | 1.12 | 63 | 70.56 | 25.9 | 8.8 | 12.9965 | YES | 300
15 | 1.05 | 63 | 66.15 | 25.9 | 8.9 | 13.3816 | YES | 300
16 | 0.74 | 63 | 46.62 | 25.6 | 8.9 | 13.1776 | YES | 300
17 | 0.97 | 63 | 61.11 | 25.7 | 8.5 | 11.5768 | YES | 300
18 | 0.98 | 63 | 61.74 | 25.6 | 8.9 | 13.5443 | YES | 300
19 | 0.6 | 63 | 37.8 | 25.5 | 8.8 | 12.5779 | YES | 300
20 | 0.98 | 63 | 61.74 | 25.5 | 8.9 | 13.6353 | YES | 300
21 | 0.88 | 63 | 55.44 | 25.4 | 8.7 | 12.5972 | YES | 300
22 | 1.03 | 63 | 64.89 | 25.2 | 8.6 | 12.5136 | YES | 300
23 | 0.89 | 63 | 56.07 | 25.2 | 8.3 | 11.0085 | YES | 300
24 | 1.1 | 63 | 69.3 | 25.5 | 8.7 | 12.8323 | YES | 300
25 | 0.91 | 63 | 57.33 | 25.5 | 8.1 | 10.0313 | YES | 300
26 | 0.83 | 63 | 52.29 | 25.5 | 8.2 | 10.3193 | YES | 300
27 | 0.97 | 63 | 61.11 | 25.5 | 8.6 | 12.1799 | YES | 300
28 | 0.94 | 63 | 59.22 | 25.5 | 8.4 | 11.2642 | YES | 300
29 | 0.9 | 63 | 56.7 | 25 | 8.3 | 11.1707 | YES | 300
30 | 0.92 | 63 | 57.96 | 25.6 | 8.6 | 12.0291 | YES | 300
31 | 0.92 | 63 | 57.96 | 25.4 | 8.2 | 10.4977 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2