## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-08-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.13 | 0.08 | 0.11 | 0.13 | 0.13
2 | 0.11 | NIS | 0.088 | NIS | NIS | NIS | 0.11
3 | NIS | 0.07 | 0.09 | 0.09 | 0.09 | 0.15 | 0.15
4 | 0.12 | 0.1 | NIS | 0.14 | NIS | NIS | 0.14
5 | NIS | NIS | 0.11 | 0.07 | 0.1 | 0.12 | 0.12
6 | 0.14 | 0.1 | NIS | NIS | NIS | NIS | 0.14
7 | NIS | 0.1 | 0.08 | 0.07 | NIS | NIS | 0.1
8 | NIS | NIS | NIS | 0.09 | 0.08 | NIS | 0.09
9 | NIS | NIS | 0.08 | 0.1 | 0.09 | NIS | 0.1
10 | 0.1 | NIS | 0.083 | 0.1 | 0.09 | NIS | 0.1
11 | NIS | NIS | 0.07 | 0.08 | NIS | NIS | 0.08
12 | NIS | NIS | 0.07 | 0.08 | 0.09 | 0.1 | 0.1
13 | 0.09 | 0.08 | 0.08 | NIS | NIS | NIS | 0.09
14 | NIS | 0.07 | 0.14 | 0.07 | 0.08 | NIS | 0.14
15 | NIS | 0.07 | 0.08 | 0.08 | 0.09 | 0.08 | 0.09
16 | NIS | NIS | 0.07 | 0.08 | NIS | NIS | 0.08
17 | NIS | 0.09 | 0.08 | 0.07 | NIS | NIS | 0.09
18 | 0.12 | 0.07 | 0.06 | NIS | NIS | NIS | 0.12
19 | NIS | 0.07 | 0.07 | 0.08 | 0.07 | NIS | 0.08
20 | NIS | 0.1 | 0.1 | 0.1 | NIS | NIS | 0.1
21 | NIS | NIS | 0.1 | 0.08 | NIS | NIS | 0.1
22 | NIS | NIS | 0.09 | 0.11 | NIS | NIS | 0.11
23 | NIS | NIS | NIS | 0.08 | 0.08 | NIS | 0.08
24 | NIS | NIS | NIS | 0.1 | 0.07 | 0.08 | 0.1
25 | 0.07 | NIS | 0.06 | 0.06 | NIS | NIS | 0.07
26 | NIS | 0.06 | 0.08 | 0.07 | 0.08 | NIS | 0.08
27 | NIS | 0.07 | 0.08 | 0.08 | NIS | NIS | 0.08
28 | NIS | 0.08 | 0.08 | 0.08 | NIS | NIS | 0.08
29 | NIS | 0.07 | 0.08 | NIS | NIS | NIS | 0.08
30 | NIS | NIS | NIS | NIS | NIS | 0.09 | 0.09
31 | 0.08 | 0.07 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-09-08
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.93 | 63 | 58.59 | 25.6 | 8.7 | 12.5006 | YES | 300
2 | 0.95 | 63 | 59.85 | 25.6 | 8.5 | 11.6282 | YES | 300
3 | 0.65 | 63 | 40.95 | 25.6 | 8.1 | 9.6686 | YES | 300
4 | 1.17 | 63 | 73.71 | 25.1 | 8.5 | 12.3331 | YES | 300
5 | 0.87 | 63 | 54.81 | 24.7 | 8.3 | 11.3594 | YES | 300
6 | 1.11 | 63 | 69.93 | 25.2 | 8.3 | 11.2907 | YES | 300
7 | 0.84 | 63 | 52.92 | 25.2 | 7.9 | 9.4187 | YES | 300
8 | 1.11 | 63 | 69.93 | 24.5 | 8.2 | 11.4012 | YES | 300
9 | 0.87 | 63 | 54.81 | 24.7 | 8.2 | 10.9422 | YES | 300
10 | 1.04 | 63 | 65.52 | 25 | 8.2 | 10.9351 | YES | 300
11 | 1 | 63 | 63 | 24.7 | 8.3 | 11.5305 | YES | 300
12 | 0.73 | 63 | 45.99 | 25.2 | 7.9 | 9.2995 | YES | 300
13 | 1.1 | 63 | 69.3 | 25.7 | 8.3 | 10.904 | YES | 300
14 | 0.83 | 63 | 52.29 | 25.9 | 7.8 | 8.6386 | YES | 300
15 | 0.94 | 63 | 59.22 | 25.9 | 7.9 | 9.0864 | YES | 300
16 | 0.95 | 63 | 59.85 | 25.6 | 7.7 | 8.609 | YES | 300
17 | 0.86 | 63 | 54.18 | 25.2 | 7.7 | 8.7545 | YES | 300
18 | 0.77 | 63 | 48.51 | 24.7 | 7.5 | 8.3104 | YES | 300
19 | 0.81 | 63 | 51.03 | 24.4 | 7.9 | 9.9088 | YES | 300
20 | 0.87 | 63 | 54.81 | 24.5 | 8 | 10.2898 | YES | 300
21 | 1.11 | 63 | 69.93 | 24.6 | 8 | 10.5074 | YES | 300
22 | 0.89 | 63 | 56.07 | 24.3 | 7.7 | 9.3389 | YES | 300
23 | 1.03 | 63 | 64.89 | 24.4 | 7.8 | 9.789 | YES | 300
24 | 1.01 | 63 | 63.63 | 24.3 | 8 | 10.5995 | YES | 300
25 | 1 | 63 | 63 | 25.3 | 7.8 | 9.1776 | YES | 300
26 | 0.76 | 63 | 47.88 | 25.5 | 8 | 9.4949 | YES | 300
27 | 0.74 | 63 | 46.62 | 25.5 | 8 | 9.4729 | YES | 300
28 | 0.79 | 63 | 49.77 | 25.4 | 8.1 | 9.9603 | YES | 300
29 | 0.77 | 63 | 48.51 | 25.1 | 7.6 | 8.3989 | YES | 300
30 | 0.93 | 63 | 58.59 | 25.1 | 8 | 9.9493 | YES | 300
31 | 1.09 | 63 | 68.67 | 24.6 | 8.2 | 11.2986 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2