## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-09-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.08 | 0.07 | 0.08 | NIS | NIS | NIS | 0.08
2 | 0.1 | 0.08 | 0.08 | 0.08 | 0.08 | NIS | 0.1
3 | NIS | 0.06 | 0.07 | 0.07 | NIS | NIS | 0.07
4 | NIS | 0.06 | 0.08 | 0.07 | 0.08 | NIS | 0.08
5 | NIS | NIS | 0.11 | 0.08 | 0.08 | NIS | 0.11
6 | NIS | NIS | 0.08 | 0.08 | NIS | NIS | 0.08
7 | NIS | NIS | 0.09 | 0.08 | NIS | NIS | 0.09
8 | NIS | 0.08 | 0.08 | NIS | NIS | NIS | 0.08
9 | NIS | 0.07 | 0.07 | 0.07 | NIS | NIS | 0.07
10 | NIS | 0.08 | 0.08 | 0.07 | 0.08 | NIS | 0.08
11 | NIS | 0.08 | 0.08 | NIS | NIS | NIS | 0.08
12 | NIS | NIS | 0.07 | 0.07 | NIS | NIS | 0.07
13 | NIS | NIS | NIS | 0.06 | 0.07 | 0.07 | 0.07
14 | 0.07 | NIS | NIS | 0.06 | NIS | NIS | 0.07
15 | 0.066 | 0.075 | 0.06 | NIS | NIS | NIS | 0.08
16 | NIS | NIS | NIS | 0.069 | 0.066 | NIS | 0.07
17 | 0.07 | NIS | 0.065 | NIS | NIS | NIS | 0.07
18 | NIS | NIS | 0.06 | 0.06 | 0.06 | 0.07 | 0.07
19 | 0.06 | 0.07 | NIS | NIS | NIS | NIS | 0.07
20 | NIS | NIS | 0.06 | 0.06 | 0.06 | 0.07 | 0.07
21 | 0.07 | 0.06 | 0.07 | NIS | NIS | NIS | 0.07
22 | NIS | NIS | 0.08 | 0.06 | 0.07 | 0.08 | 0.08
23 | 0.07 | 0.07 | 0.08 | NIS | NIS | NIS | 0.08
24 | NIS | 0.07 | 0.12 | 0.056 | 0.043 | 0.07 | 0.12
25 | NIS | NIS | 0.08 | NIS | NIS | NIS | 0.08
26 | NIS | 0.07 | 0.06 | 0.06 | NIS | NIS | 0.07
27 | NIS | 0.08 | 0.07 | 0.07 | 0.08 | NIS | 0.08
28 | NIS | NIS | 0.07 | 0.09 | 0.08 | NIS | 0.09
29 | NIS | 0.07 | 0.07 | 0.07 | NIS | NIS | 0.07
30 | NIS | NIS | 0.06 | 0.07 | NIS | NIS | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-10-06
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 63 | 56.7 | 24.7 | 8.3 | 11.3987 | YES | 300
2 | 1.09 | 63 | 68.67 | 24.7 | 8.2 | 11.2228 | YES | 300
3 | 0.93 | 63 | 58.59 | 24.8 | 7.8 | 9.4176 | YES | 300
4 | 0.94 | 63 | 59.22 | 24.6 | 7.6 | 8.8631 | YES | 300
5 | 1.13 | 63 | 71.19 | 24.7 | 7.7 | 9.3452 | YES | 300
6 | 1.12 | 63 | 70.56 | 24.6 | 7.6 | 9.0502 | YES | 300
7 | 1.13 | 63 | 71.19 | 24.3 | 7.6 | 9.2472 | YES | 300
8 | 0.83 | 63 | 52.29 | 24.3 | 8.2 | 11.1896 | YES | 300
9 | 0.9 | 63 | 56.7 | 23.9 | 8 | 10.7523 | YES | 300
10 | 0.96 | 63 | 60.48 | 23.5 | 7.8 | 10.3197 | YES | 300
11 | 1.05 | 63 | 66.15 | 23.1 | 7.7 | 10.3185 | YES | 300
12 | 1.02 | 63 | 64.26 | 23.1 | 7.9 | 11.0833 | YES | 300
13 | 1.16 | 63 | 73.08 | 22.7 | 7.6 | 10.3411 | YES | 300
14 | 1.15 | 63 | 72.45 | 22.4 | 7.7 | 10.9431 | YES | 300
15 | 1.18 | 63 | 74.34 | 22 | 8 | 12.618 | YES | 300
16 | 1.19 | 63 | 74.97 | 21.6 | 7.7 | 11.6022 | YES | 300
17 | 1.22 | 63 | 76.86 | 21.5 | 7.8 | 12.1667 | YES | 300
18 | 1.06 | 63 | 66.78 | 22.1 | 7.6 | 10.6453 | YES | 300
19 | 1.16 | 63 | 73.08 | 21.7 | 7.5 | 10.6563 | YES | 300
20 | 1.05 | 63 | 66.15 | 21.7 | 7.6 | 10.9238 | YES | 300
21 | 1.2 | 63 | 75.6 | 21.5 | 7.5 | 10.851 | YES | 300
22 | 1.16 | 63 | 73.08 | 21.2 | 7.6 | 11.442 | YES | 300
23 | 0.93 | 63 | 58.59 | 20.5 | 7.4 | 10.8389 | YES | 300
24 | 0.93 | 63 | 58.59 | 20.6 | 7.4 | 10.7661 | YES | 300
25 | 1.11 | 63 | 69.93 | 20.8 | 7.6 | 11.6868 | YES | 300
26 | 0.9 | 63 | 56.7 | 20.3 | 7.7 | 12.2472 | YES | 300
27 | 0.85 | 63 | 53.55 | 20.1 | 7.4 | 11.0331 | YES | 300
28 | 1.2 | 63 | 75.6 | 20 | 7.4 | 11.5639 | YES | 300
29 | 1.08 | 63 | 68.04 | 20.3 | 7.3 | 10.7666 | YES | 300
30 | 1.06 | 63 | 66.78 | 19.7 | 7.5 | 12.0533 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2