## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-10-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | 0.07 | 0.067 | 0.067 | NIS | NIS | 0.07
2 | NIS | 0.07 | 0.06 | 0.06 | NIS | NIS | 0.07
3 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
4 | NIS | NIS | NIS | 0.06 | 0.07 | 0.06 | 0.07
5 | NIS | NIS | NIS | 0.06 | 0.05 | NIS | 0.06
6 | NIS | 0.05 | 0.06 | NIS | NIS | NIS | 0.06
7 | NIS | 0.06 | 0.06 | 0.06 | 0.06 | NIS | 0.06
8 | NIS | 0.05 | 0.06 | 0.07 | NIS | NIS | 0.07
9 | NIS | NIS | 0.06 | 0.06 | 0.06 | 0.07 | 0.07
10 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
11 | NIS | NIS | 0.06 | 0.06 | 0.06 | NIS | 0.06
12 | NIS | NIS | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
13 | NIS | NIS | 0.061 | NIS | NIS | NIS | 0.06
14 | NIS | NIS | NIS | 0.09 | 0.1 | 0.06 | 0.1
15 | 0.06 | 0.05 | 0.05 | NIS | NIS | NIS | 0.06
16 | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
17 | NIS | NIS | 0.06 | 0.05 | 0.06 | NIS | 0.06
18 | NIS | 0.06 | NIS | NIS | 0.05 | 0.05 | 0.06
19 | NIS | 0.05 | NIS | 0.05 | NIS | NIS | 0.05
20 | NIS | NIS | 0.05 | 0.06 | 0.07 | 0.06 | 0.07
21 | 0.06 | NIS | 0.05 | 0.07 | NIS | NIS | 0.07
22 | NIS | 0.05 | 0.05 | 0.06 | NIS | NIS | 0.06
23 | NIS | 0.05 | 0.06 | 0.06 | 0.06 | NIS | 0.06
24 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
25 | NIS | NIS | 0.05 | 0.05 | NIS | NIS | 0.05
26 | NIS | NIS | 0.05 | NIS | NIS | NIS | 0.05
27 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | NIS | 0.05
28 | NIS | NIS | 0.05 | NIS | NIS | NIS | 0.05
29 | NIS | NIS | 0.05 | 0.05 | 0.05 | NIS | 0.05
30 | NIS | 0.05 | 0.05 | 0.05 | 0.05 | NIS | 0.05
31 | NIS | NIS | 0.05 | 0.05 | 0.05 | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-11-03
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.91 | 63 | 57.33 | 19.3 | 7.5 | 12.1703 | YES | 469
2 | 0.85 | 63 | 53.55 | 18.9 | 7.4 | 11.9613 | YES | 469
3 | 0.88 | 63 | 55.44 | 18.9 | 7.5 | 12.4588 | YES | 469
4 | 0.92 | 63 | 57.96 | 18.8 | 7.4 | 12.1391 | YES | 469
5 | 0.81 | 63 | 51.03 | 18.8 | 7.6 | 12.9148 | YES | 469
6 | 0.61 | 63 | 38.43 | 18.3 | 7.8 | 14.0606 | YES | 469
7 | 0.75 | 63 | 47.25 | 18 | 7.6 | 13.5328 | YES | 469
8 | 0.56 | 63 | 35.28 | 18.1 | 7.5 | 12.6726 | YES | 469
9 | 0.85 | 63 | 53.55 | 18.3 | 7.6 | 13.4162 | YES | 469
10 | 0.94 | 63 | 59.22 | 17.6 | 7.5 | 13.6868 | YES | 469
11 | 0.87 | 63 | 54.81 | 17.5 | 7.5 | 13.6689 | YES | 469
12 | 0.83 | 63 | 52.29 | 17 | 7.5 | 14.0695 | YES | 469
13 | 0.96 | 63 | 60.48 | 16.6 | 7.6 | 15.221 | YES | 469
14 | 0.65 | 63 | 40.95 | 17 | 7.5 | 13.7831 | YES | 469
15 | 0.83 | 63 | 52.29 | 15.6 | 7.6 | 16.0317 | YES | 469
16 | 0.86 | 63 | 54.18 | 15.8 | 7.6 | 15.8735 | YES | 469
17 | 0.97 | 63 | 61.11 | 16.1 | 7.4 | 14.6294 | YES | 469
18 | 0.87 | 63 | 54.81 | 16 | 7.5 | 15.1106 | YES | 469
19 | 0.88 | 63 | 55.44 | 16.1 | 7.4 | 14.4799 | YES | 469
20 | 0.84 | 63 | 52.92 | 15.9 | 7.6 | 15.7321 | YES | 469
21 | 0.83 | 63 | 52.29 | 15.6 | 7.5 | 15.4488 | YES | 469
22 | 0.69 | 63 | 43.47 | 15.3 | 7.5 | 15.5117 | YES | 469
23 | 0.73 | 63 | 45.99 | 15.2 | 7.6 | 16.2785 | YES | 469
24 | 1.01 | 63 | 63.63 | 15.5 | 7.5 | 15.8743 | YES | 469
25 | 0.96 | 63 | 60.48 | 15.5 | 7.5 | 15.7842 | YES | 469
26 | 1.32 | 63 | 83.16 | 15.3 | 7.4 | 16.0595 | YES | 469
27 | 0.79 | 63 | 49.77 | 14.1 | 7.5 | 16.9953 | YES | 469
28 | 0.91 | 63 | 57.33 | 14.5 | 7.4 | 16.1667 | YES | 469
29 | 0.66 | 63 | 41.58 | 14.2 | 7.5 | 16.6348 | YES | 469
30 | 0.55 | 63 | 34.65 | 14.1 | 7.4 | 15.9369 | YES | 469
31 | 0.81 | 63 | 51.03 | 13.9 | 7.6 | 17.9117 | YES | 469
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2