## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-11-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 0.046 | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.046 | 0.05 | 0.05 | NIS | 0.05
2 | NIS | NIS | 0.057 | 0.05 | 0.05 | 0.05 | 0.05
3 | 0.05 | NIS | 0.049 | NIS | NIS | NIS | 0.05
4 | 0.05 | 0.04 | 0.048 | 0.04 | 0.04 | 0.04 | 0.05
5 | NIS | NIS | NIS | 0.04 | NIS | NIS | 0.04
6 | NIS | 0.04 | 0.05 | 0.045 | NIS | NIS | 0.05
7 | NIS | 0.04 | 0.05 | 0.05 | NIS | NIS | 0.05
8 | NIS | 0.05 | 0.05 | 0.054 | NIS | NIS | 0.05
9 | NIS | 0.05 | 0.05 | 0.05 | NIS | NIS | 0.05
10 | NIS | NIS | NIS | 0.065 | 0.05 | 0.05 | 0.07
11 | 0.06 | 0.05 | 0.05 | NIS | 0.05 | NIS | 0.06
12 | NIS | 0.05 | 0.071 | 0.052 | 0.05 | NIS | 0.07
13 | NIS | NIS | 0.047 | NIS | NIS | NIS | 0.05
14 | NIS | NIS | NIS | 0.054 | NIS | NIS | 0.05
15 | NIS | NIS | NIS | 0.05 | 0.057 | NIS | 0.06
16 | NIS | NIS | 0.065 | 0.055 | 0.05 | NIS | 0.07
17 | NIS | 0.05 | 0.06 | 0.055 | NIS | NIS | 0.06
18 | 0.05 | 0.06 | NIS | 0.062 | 0.054 | NIS | 0.06
19 | NIS | 0.05 | 0.06 | 0.06 | 0.049 | NIS | 0.06
20 | NIS | 0.05 | 0.06 | 0.05 | NIS | NIS | 0.06
21 | NIS | 0.05 | 0.054 | 0.054 | NIS | NIS | 0.05
22 | NIS | NIS | 0.057 | 0.05 | 0.05 | 0.06 | 0.06
23 | NIS | NIS | 0.052 | 0.05 | NIS | NIS | 0.05
24 | NIS | 0.05 | NIS | 0.05 | NIS | NIS | 0.05
25 | NIS | 0.05 | 0.05 | 0.059 | 0.053 | 0.05 | 0.06
26 | NIS | NIS | 0.056 | NIS | NIS | NIS | 0.06
27 | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.06 | 0.06
28 | 0.05 | 0.05 | 0.05 | NIS | NIS | NIS | 0.05
29 | NIS | NIS | 0.05 | 0.056 | 0.052 | NIS | 0.06
30 | NIS | NIS | 0.05 | 0.06 | NIS | NIS | 0.06
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2025-12-01
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-11-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.89 | 63 | 56.07 | 14.3 | 7.5 | 16.9623 | YES | 469
2 | 0.83 | 63 | 52.29 | 14.2 | 7.5 | 16.9595 | YES | 469
3 | 0.89 | 63 | 56.07 | 14 | 7.5 | 17.3043 | YES | 469
4 | 0.83 | 63 | 52.29 | 14 | 7.4 | 16.5629 | YES | 469
5 | 0.9 | 63 | 56.7 | 13.8 | 7.6 | 18.2163 | YES | 469
6 | 0.86 | 63 | 54.18 | 14.3 | 7.5 | 16.9045 | YES | 469
7 | 0.74 | 63 | 46.62 | 13.8 | 7.5 | 17.2398 | YES | 469
8 | 0.7 | 63 | 44.1 | 13.8 | 7.5 | 17.1616 | YES | 469
9 | 0.77 | 63 | 48.51 | 14.2 | 7.4 | 16.2325 | YES | 469
10 | 0.83 | 63 | 52.29 | 14 | 7.6 | 17.8335 | YES | 469
11 | 0.74 | 63 | 46.62 | 14.1 | 7.5 | 16.899 | YES | 469
12 | 0.72 | 63 | 45.36 | 14.3 | 7.5 | 16.6375 | YES | 469
13 | 0.85 | 63 | 53.55 | 14 | 7.5 | 17.2258 | YES | 469
14 | 0.86 | 63 | 54.18 | 13.8 | 7.2 | 15.6407 | YES | 469
15 | 0.86 | 63 | 54.18 | 14 | 7.3 | 16.0158 | YES | 469
16 | 0.83 | 63 | 52.29 | 14.1 | 7.4 | 16.4529 | YES | 469
17 | 0.7 | 63 | 44.1 | 13.9 | 7.7 | 18.3547 | YES | 469
18 | 0.66 | 63 | 41.58 | 13.5 | 7.5 | 17.4282 | YES | 469
19 | 0.67 | 63 | 42.21 | 13.8 | 7.3 | 15.8834 | YES | 469
20 | 0.77 | 63 | 48.51 | 13.8 | 7.2 | 15.4812 | YES | 469
21 | 0.74 | 63 | 46.62 | 12.7 | 7.5 | 18.5478 | YES | 469
22 | 0.93 | 63 | 58.59 | 12.8 | 7.4 | 18.1444 | YES | 469
23 | 1 | 63 | 63 | 12.6 | 7.4 | 18.5338 | YES | 469
24 | 0.72 | 63 | 45.36 | 12.6 | 7.7 | 20.0544 | YES | 469
25 | 0.84 | 63 | 52.92 | 12.7 | 7.4 | 18.0798 | YES | 469
26 | 0.89 | 63 | 56.07 | 11.7 | 7.4 | 19.6036 | YES | 469
27 | 0.9 | 63 | 56.7 | 12.2 | 7.3 | 18.354 | YES | 469
28 | 0.85 | 63 | 53.55 | 11.5 | 7.3 | 19.0987 | YES | 469
29 | 0.92 | 63 | 57.96 | 12.5 | 7.3 | 17.8187 | YES | 469
30 | 0.92 | 63 | 57.96 | 12.2 | 7.4 | 19.0402 | YES | 469
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2