## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-01-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8AM (NTU) | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | NIS | 0.059 | 0.05 | 0.05 | 0.06
2 | 0.05 | NIS | NIS | NIS | NIS | NIS | 0.05
3 | NIS | NIS | NIS | 0.07 | 0.055 | 0.063 | 0.07
4 | 0.06 | 0.08 | 0.057 | NIS | NIS | NIS | 0.08
5 | NIS | 0.06 | 0.058 | 0.067 | 0.062 | 0.05 | 0.07
6 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
7 | NIS | 0.05 | 0.059 | 0.066 | NIS | NIS | 0.07
8 | NIS | 0.06 | 0.06 | 0.056 | NIS | NIS | 0.06
9 | NIS | 0.06 | 0.075 | 0.058 | NIS | NIS | 0.08
10 | NIS | NIS | 0.06 | 0.057 | NIS | NIS | 0.06
11 | NIS | 0.08 | 0.06 | 0.06 | 0.08 | NIS | 0.08
12 | NIS | NIS | 0.07 | 0.057 | 0.07 | NIS | 0.07
13 | NIS | NIS | 0.073 | 0.058 | 0.07 | NIS | 0.07
14 | NIS | NIS | 0.06 | 0.074 | 0.051 | NIS | 0.07
15 | NIS | NIS | 0.07 | 0.09 | 0.049 | NIS | 0.09
16 | NIS | NIS | 0.083 | 0.051 | 0.06 | NIS | 0.08
17 | NIS | NIS | NIS | 0.09 | 0.06 | 0.06 | 0.09
18 | 0.06 | NIS | NIS | 0.06 | NIS | NIS | 0.06
19 | NIS | NIS | NIS | 0.07 | 0.06 | 0.06 | 0.07
20 | 0.07 | 0.06 | NIS | NIS | NIS | NIS | 0.07
21 | NIS | NIS | 0.089 | 0.07 | 0.058 | NIS | 0.09
22 | NIS | NIS | 0.07 | 0.065 | NIS | 0.07 | 0.07
23 | 0.07 | 0.07 | NIS | NIS | NIS | NIS | 0.07
24 | NIS | NIS | 0.07 | 0.065 | 0.09 | NIS | 0.09
25 | 0.07 | 0.07 | 0.095 | 0.06 | 0.06 | 0.07 | 0.1
26 | 0.07 | NIS | 0.07 | 0.068 | 0.063 | 0.08 | 0.08
27 | NIS | NIS | NIS | 0.07 | NIS | NIS | 0.07
28 | NIS | NIS | 0.05 | 0.06 | 0.08 | 0.06 | 0.08
29 | 0.07 | 0.07 | NIS | NIS | 0.055 | NIS | 0.07
30 | NIS | 0.07 | 0.064 | 0.069 | NIS | NIS | 0.07
31 | NIS | 0.072 | 0.07 | 0.08 | 0.06 | NIS | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 2/2/2026
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2025-11-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.18 | 63 | 74.34 | 9.3 | 7.5 | 24.5775 | YES | 469
2 | 1.28 | 63 | 80.64 | 9.1 | 7.3 | 23.4672 | YES | 469
3 | 1.15 | 63 | 72.45 | 9 | 7.3 | 23.277 | YES | 469
4 | 1.16 | 63 | 73.08 | 9.1 | 7.4 | 23.9836 | YES | 469
5 | 1.03 | 63 | 64.89 | 9.7 | 7.5 | 23.526 | YES | 469
6 | 1.14 | 63 | 71.82 | 10 | 7.4 | 22.5421 | YES | 469
7 | 1.09 | 63 | 68.67 | 10.2 | 7.4 | 22.1207 | YES | 469
8 | 1.09 | 63 | 68.67 | 9.6 | 7.4 | 23.0163 | YES | 469
9 | 1.01 | 63 | 63.63 | 8.7 | 7.5 | 25.0897 | YES | 469
10 | 1.28 | 63 | 80.64 | 9 | 7.9 | 29.2769 | YES | 469
11 | 1.13 | 63 | 71.19 | 9.3 | 7.3 | 22.767 | YES | 469
12 | 1.2 | 63 | 75.6 | 8.9 | 7.5 | 25.3008 | YES | 469
13 | 1.24 | 63 | 78.12 | 9.3 | 7.5 | 24.7466 | YES | 469
14 | 1.23 | 63 | 77.49 | 8.9 | 7.6 | 26.3109 | YES | 469
15 | 1.23 | 63 | 77.49 | 8.6 | 7.7 | 27.8274 | YES | 469
16 | 1.16 | 63 | 73.08 | 8.8 | 7.5 | 25.3542 | YES | 469
17 | 1.25 | 63 | 78.75 | 8.9 | 7.5 | 25.4462 | YES | 469
18 | 1.25 | 63 | 78.75 | 8.3 | 7 | 22.1828 | YES | 469
19 | 1.17 | 63 | 73.71 | 8.1 | 7.5 | 26.603 | YES | 469
20 | 1.27 | 63 | 80.01 | 7.8 | 7.6 | 28.465 | YES | 469
21 | 1.02 | 63 | 64.26 | 8.2 | 7.6 | 26.9196 | YES | 469
22 | 1.19 | 63 | 74.97 | 7.5 | 7.6 | 28.7804 | YES | 469
23 | 1.25 | 63 | 78.75 | 7.2 | 7.6 | 29.5759 | YES | 469
24 | 0.96 | 63 | 60.48 | 7.2 | 7.6 | 28.5984 | YES | 469
25 | 0.95 | 63 | 59.85 | 7 | 7.6 | 28.9543 | YES | 469
26 | 1.21 | 63 | 76.23 | 6.9 | 7.6 | 30.0439 | YES | 469
27 | 1.1 | 63 | 69.3 | 7 | 7.6 | 29.4622 | YES | 469
28 | 1.1 | 63 | 69.3 | 6.8 | 7.6 | 29.8643 | YES | 469
29 | 1.13 | 63 | 71.19 | 7.3 | 7.6 | 28.9704 | YES | 469
30 | 1.17 | 63 | 73.71 | 7.1 | 7.5 | 28.4571 | YES | 469
31 | 0.98 | 63 | 61.74 | 7.5 | 7.5 | 27.0988 | YES | 469
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2