## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year:
System Name: | City of Gold Beach |  |  | ID#: 4101059 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | off | off | off | 0.023 | 0.022 | off | 0.035
2 | off | off | off | 0.02 | 0.03 | off | 0.03
3 | off | off | off | 0.016 | 0.016 | 0.018 | 0.022
4 | off | off | off | 0.018 | 0.018 | 0.016 | 0.04
5 | off | off | off | 0.017 | 0.016 | 0.021 | 0.025
6 | off | off | off | 0.023 | 0.016 | off | 0.022
7 | off | off | off | 0.041 | 0.017 | 0.031 | 0.041
8 | off | off | off | 0.035 | 0.08 | off | 0.08
9 | off | off | 0.019 | 0.021 | off | off | 0.05
10 | 0.035 | 0.019 | off | 0.019 | 0.019 | 0.02 | 0.022
11 | off | off | off | 0.023 | 0.019 | 0.019 | 0.051
12 | off | off | off | 0.02 | 0.022 | off | 0.022
13 | off | off | 0.021 | off | 0.016 | 0.031 | 0.031
14 | off | off | off | 0.023 | 0.025 | 0.032 | 0.04
15 | off | off | off | 0.019 | 0.02 | off | 0.035
16 | off | off | 0.016 | 0.019 | off | off | 0.021
17 | 0.038 | off | off | 0.028 | 0.021 | 0.019 | 0.03
18 | off | off | off | 0.022 | 0.025 | off | 0.042
19 | off | 0.022 | off | 0.022 | 0.024 | 0.028 | 0.044
20 | off | off | off | 0.028 | 0.02 | 0.02 | 0.03
21 | off | off | off | 0.026 | 0.028 | 0.024 | 0.08
22 | off | off | off | 0.028 | 0.06 | 0.023 | 0.06
23 | off | off | 0.02 | 0.016 | 0.016 | 0.016 | 0.021
24 | off | off | off | 0.016 | 0.042 | off | 0.042
25 | off | off | off | 0.02 | 0.016 | 0.016 | 0.041
26 | 0.016 | 0.016 | 0.016 | 0.018 | 0.016 | 0.016 | 0.05
27 | 0.016 | 0.016 | 0.016 | 0.016 | 0.03 | 0.016 | 0.03
28 | 0.016 | 0.016 | 0.016 | 0.016 | 0.016 | 0.018 | 0.022
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Will Newdall
[5 empty] | SIGNATURE: |  |  | 2021-03-04
[5 empty] | PHONE #: (541 )247-7459 |  |  | CERT #:FE0054
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | City of Gold Beach |  | ID#: 4101059 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.96 | 60 | 57.6 | 10.5 | 7.26 | 20.3516 | YES | 700
2 | 0.87 | 60 | 52.2 | 11.3 | 7.17 | 18.5398 | YES | 700
3 | 0.89 | 60 | 53.4 | 12.3 | 7.17 | 17.422 | YES | 700
4 | 0.96 | 60 | 57.6 | 12.9 | 7.11 | 16.2475 | YES | 700
5 | 0.84 | 60 | 50.4 | 13 | 7.1 | 15.8618 | YES | 700
6 | 0.97 | 60 | 58.2 | 12 | 7.1 | 17.4936 | YES | 700
7 | 0.95 | 60 | 57 | 10.9 | 7.16 | 19.13 | YES | 700
8 | 0.96 | 60 | 57.6 | 10.6 | 7.09 | 19.0607 | YES | 700
9 | 0.88 | 60 | 52.8 | 10.6 | 7.12 | 19.089 | YES | 700
10 | 0.84 | 60 | 50.4 | 10.7 | 7.1 | 18.7517 | YES | 700
11 | 1.04 | 60 | 62.4 | 11.2 | 7.17 | 19.0154 | YES | 700
12 | 1.04 | 60 | 62.4 | 10.7 | 7.21 | 19.9183 | YES | 700
13 | 0.94 | 60 | 56.4 | 10.7 | 7.19 | 19.561 | YES | 700
14 | 0.94 | 60 | 56.4 | 10.8 | 7.16 | 19.2332 | YES | 700
15 | 0.98 | 60 | 58.8 | 12.9 | 7.17 | 16.65 | YES | 700
16 | 0.88 | 60 | 52.8 | 10.8 | 7.16 | 19.1053 | YES | 700
17 | 0.97 | 60 | 58.2 | 12.4 | 7.17 | 17.4634 | YES | 700
18 | 0.93 | 60 | 55.8 | 10.9 | 7.12 | 18.8255 | YES | 700
19 | 0.88 | 60 | 52.8 | 12.8 | 7.11 | 16.2079 | YES | 700
20 | 0.82 | 60 | 49.2 | 12.3 | 7.15 | 17.1711 | YES | 700
21 | 0.94 | 60 | 56.4 | 12.1 | 7.13 | 17.5032 | YES | 700
22 | 0.94 | 60 | 56.4 | 13 | 7.17 | 16.4644 | YES | 700
23 | 0.84 | 60 | 50.4 | 10.9 | 7.13 | 18.703 | YES | 700
24 | 1.03 | 60 | 61.8 | 11.1 | 7.11 | 18.7257 | YES | 700
25 | 0.89 | 60 | 53.4 | 10.5 | 7.12 | 19.2347 | YES | 700
26 | 0.96 | 60 | 57.6 | 10.7 | 7.18 | 19.5367 | YES | 700
27 | 0.82 | 60 | 49.2 | 11.4 | 7.17 | 18.3188 | YES | 700
28 | 0.82 | 60 | 49.2 | 11.7 | 7.11 | 17.6023 | YES | 700
29
30
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2