## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-09-01
System Name: | City of Gold Beach |  |  | ID#: 4101059 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.04 | 0.01 | 0.01 | OFF | 0.11
2 | 0.01 | OFF | 0.02 | 0.01 | 0.01 | 0.01 | 0.05
3 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.02 | 0.04
4 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.03
5 | OFF | 0.01 | 0.02 | 0.01 | 0.01 | 0.01 | 0.03
6 | OFF | OFF | 0.03 | 0.01 | 0.01 | OFF | 0.05
7 | 0.01 | OFF | 0.02 | 0.01 | 0.01 | 0.01 | 0.04
8 | 0.01 | OFF | 0.01 | 0.01 | 0.02 | 0.01 | 0.04
9 | OFF | 0.01 | 0.01 | 0.01 | 0.01 | OFF | 0.05
10 | OFF | 0.02 | OFF | 0.01 | 0.01 | 0.01 | 0.04
11 | 0.01 | OFF | OFF | 0.01 | 0.02 | 0.01 | 0.04
12 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.04
13 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.29
14 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.06
15 | OFF | OFF | OFF | 0.02 | 0.02 | 0.01 | 0.05
16 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.03
17 | OFF | 0.02 | 0.01 | 0.01 | 0.01 | OFF | 0.04
18 | OFF | OFF | 0.01 | 0.02 | 0.01 | 0.01 | 0.06
19 | OFF | OFF | 0.03 | 0.01 | 0.01 | OFF | 0.04
20 | OFF | OFF | 0.02 | 0.01 | 0.01 | 0.01 | 0.36
21 | OFF | OFF | 0.01 | 0.02 | 0.02 | 0.01 | 0.06
22 | OFF | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.03
23 | OFF | OFF | 0.02 | 0.01 | 0.01 | 0.02 | 0.07
24 | 0.01 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.03
25 | 0.01 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.55
26 | OFF | OFF | 0.02 | 0.01 | 0.01 | 0.02 | 0.33
27 | OFF | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.06
28 | OFF | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.04
29 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.04
30 | OFF | OFF | 0.02 | 0.01 | 0.02 | 0.01 | 0.85
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Will Newdall
[5 empty] | SIGNATURE: |  |  | 2024-09-01
[5 empty] | PHONE #: (541 )247-7459 |  |  | CERT #:FE0054
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | City of Gold Beach |  | ID#: 4101059 |  | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.97 | 60 | 58.2 | 18.9 | 7.1 | 10.8405 | YES | 700
2 | 0.99 | 60 | 59.4 | 17.1 | 6.95 | 11.5968 | YES | 700
3 | 1.05 | 60 | 63 | 20.3 | 7.03 | 9.6951 | YES | 700
4 | 0.97 | 60 | 58.2 | 22.3 | 7.07 | 8.513 | YES | 700
5 | 0.97 | 60 | 58.2 | 20.5 | 7.07 | 9.6202 | YES | 700
6 | 0.99 | 60 | 59.4 | 18.8 | 6.93 | 10.2636 | YES | 700
7 | 0.99 | 60 | 59.4 | 20 | 7.02 | 9.7888 | YES | 700
8 | 1.09 | 60 | 65.4 | 19.8 | 6.94 | 9.7402 | YES | 700
9 | 0.89 | 60 | 53.4 | 20.4 | 6.95 | 9.1723 | YES | 700
10 | 0.89 | 60 | 53.4 | 18.2 | 6.94 | 10.6052 | YES | 700
11 | 0.91 | 60 | 54.6 | 19.5 | 7.09 | 10.2997 | YES | 700
12 | 0.97 | 60 | 58.2 | 20 | 7.06 | 9.9142 | YES | 700
13 | 0.98 | 60 | 58.8 | 22.5 | 7.04 | 8.3126 | YES | 700
14 | 0.91 | 60 | 54.6 | 22.7 | 7.02 | 8.0718 | YES | 700
15 | 1 | 60 | 60 | 21.2 | 7.02 | 9.0342 | YES | 700
16 | 0.92 | 60 | 55.2 | 20.2 | 7.09 | 9.8348 | YES | 700
17 | 0.97 | 60 | 58.2 | 20.7 | 7 | 9.2437 | YES | 700
18 | 0.93 | 60 | 55.8 | 24.1 | 7.1 | 7.5788 | YES | 700
19 | 0.96 | 60 | 57.6 | 20 | 7.11 | 10.0905 | YES | 700
20 | 0.93 | 60 | 55.8 | 19.4 | 7.09 | 10.3935 | YES | 700
21 | 0.95 | 60 | 57 | 21.6 | 7.11 | 9.043 | YES | 700
22 | 0.96 | 60 | 57.6 | 20.8 | 7.09 | 9.4868 | YES | 700
23 | 0.9 | 60 | 54 | 25.7 | 7.13 | 6.8441 | YES | 0
24 | 0.86 | 60 | 51.6 | 20.5 | 7.05 | 9.4273 | YES | 700
25 | 0.95 | 60 | 57 | 19.2 | 6.98 | 10.1322 | YES | 700
26 | 0.88 | 60 | 52.8 | 21 | 6.93 | 8.7294 | YES | 700
27 | 0.93 | 60 | 55.8 | 18.6 | 7.06 | 10.8475 | YES | 700
28 | 0.93 | 60 | 55.8 | 18 | 7.03 | 11.1691 | YES | 700
29 | 0.9 | 60 | 54 | 19.3 | 7.06 | 10.3111 | YES | 700
30 | 0.95 | 60 | 57 | 19.5 | 7.04 | 10.155 | YES | 700
31 | [6 empty] | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | . | [5 empty] | Revised September 2016
PAGE 2 of 2