## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-01-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
2 | [5 empty] | 0.03 | 0.03
3 | [6 empty] | 0.03
4 | 0.03 | 0.03 | 0.03 | 0.132 | 0.132 | 0.132 | 0.132
5 | [6 empty] | 0.13
6 |  |  |  | 0.125 | 0.125 | 0.125 | 0.125
7 | 0.12 | 0.12 | 0.12 |  |  |  | 0.12
8 | [6 empty] | 0.122
9 | 0.122 | 0.122 | 0.122 | 0.122 | 0.122 | 0.122 | 0.122
10 |  |  |  | 0.049 | 0.049 | 0.049 | 0.049
11 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049
12 | [6 empty] | 0.049
13 | [6 empty] | 0.038
14 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038
15 | 0.038 | 0.038 | 0.038 |  |  |  | 0.038
16 |  |  |  | 0.025 | 0.025 | 0.025 | 0.025
17 | 0.025 | 0.025 | 0.025 | 0.025 |  |  | 0.025
18 | 0.025 | 0.025 | 0.025 | 0.025 |  |  | 0.025
19 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.025
20 | [6 empty] | 0.028
21 | [6 empty] | 0.028
22 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
23 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
24 | [6 empty] | 0.029
25 |  | 0.029 | 0.029 | 0.029 | 0.029 |  | 0.029
26 | [6 empty] | 0.029
27 | 0.029 | 0.029 | 0.029 | 0.029 |  |  | 0.029
28 | [6 empty] | 0.035
29 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035 | 0.035
30 | [6 empty] | 0.037
31 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:02/10/2021
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2021-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—8 am | 0.98 | 259 | 253.82 | 14.6 | 6.8 | 25.9115 | YES | 8.26
2—8 am | 0.99 | 259 | 256.41 | 14.5 | 6.86 | 26.7054 | YES | 8.47
3--8 am | 0.99 | 259 | 256.41 | 14.7 | 6.9 | 26.7451 | YES | 8.26
4—8 am | 1 | 259 | 259 | 16.2 | 6.88 | 24.0324 | YES | 9.51
5—8 am | 0.99 | 259 | 256.41 | 15.4 | 6.9 | 25.5191 | YES | 9.38
6—8 am | 0.95 | 259 | 246.05 | 15.9 | 6.93 | 24.8404 | YES | 8.82
7--8 am | 0.99 | 259 | 256.41 | 1.58 | 6.91 | 65.4972 | YES | 7.71
8--8 am | 1.01 | 259 | 261.59 | 15.6 | 6.9 | 25.2368 | YES | 9.1
9—8 am | 1 | 259 | 259 | 16 | 6.97 | 25.1889 | YES | 10.21
10—8 am | 0.99 | 259 | 256.41 | 15.9 | 7 | 25.6141 | YES | 7.01
11—8 am | 1.03 | 259 | 266.77 | 15.8 | 7.01 | 26.0015 | YES | 9.38
12—8 am | 1 | 259 | 259 | 15.6 | 7 | 26.1645 | YES | 9.17
13—8 am | 1 | 259 | 259 | 16.2 | 6.91 | 24.303 | YES | 9.24
14—8 am | 1.03 | 259 | 266.77 | 16.3 | 6.96 | 24.6796 | YES | 9.44
15—8 am | 1 | 259 | 259 | 16.8 | 6.5 | 20.0185 | YES | 7.99
16—8 am | 1.01 | 259 | 261.59 | 16.7 | 6.52 | 20.3298 | YES | 6.18
17—8 am | 1.02 | 259 | 264.18 | 16.6 | 6.7 | 21.9219 | YES | 9.03
18—8 am | 1.03 | 259 | 266.77 | 16.8 | 6.77 | 22.2282 | YES | 10.42
19—8 am | 1.01 | 259 | 261.59 | 16.7 | 6.8 | 22.579 | YES | 8.26
20—8 am | 1.04 | 259 | 269.36 | 16.5 | 6.85 | 23.3973 | YES | 8.47
21—8 am | 1 | 259 | 259 | 16.6 | 6.9 | 23.5701 | YES | 8.26
22—8 am | 1.01 | 259 | 261.59 | 16.4 | 7 | 24.8258 | YES | 7.71
23—8 am | 1.03 | 259 | 266.77 | 13.6 | 7.01 | 30.1242 | YES | 8.19
24—8 am | 1.02 | 259 | 264.18 | 13.5 | 7.03 | 30.5168 | YES | 8.33
25—8 am | 1 | 259 | 259 | 13.7 | 7 | 29.7111 | YES | 7.78
26—8 am | 1 | 259 | 259 | 13.5 | 7.01 | 30.2224 | YES | 7.64
27—8 am | 1.06 | 259 | 274.54 | 13.6 | 7.02 | 30.3396 | YES | 8.19
28—8 am | 1.02 | 259 | 264.18 | 13.7 | 7 | 29.779 | YES | 7.99
29—8 am | 1.04 | 259 | 269.36 | 13.6 | 7 | 30.0469 | YES | 10.07
30—8 am | 1.02 | 259 | 264.18 | 15.3 | 7.01 | 26.8567 | YES | 9.03
31—8 am | 1.04 | 259 | 269.36 | 15.2 | 7.02 | 27.2 | YES | 7.99
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2