## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-04-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.028 | 0.028 | 0.029 | 0.029
2 | 0.027 |  | 0.027 | 0.026 | 0.026 | 0.025 | 0.028
3 |  |  |  |  | 0.028 | 0.028 | 0.028
4 | 0.028 | 0.026 | 0.025 | 0.026 | 0.026 | 0.027 | 0.027
5 | 0.03 |  |  | 0.029 | 0.029 | 0.03 | 0.03
6 |  |  |  | 0.026 | 0.027 | 0.029 | 0.029
7 | 0.029 |  |  | 0.028 | 0.029 | 0.029 | 0.029
8 |  |  |  |  | 0.03 | 0.031 | 0.031
9 | 0.032 | 0.033 | 0.034 |  |  |  | 0.034
10 | [5 empty] | 0.029 | 0.029
11 | 0.03 | 0.031 |  |  | 0.031 | 0.032 | 0.032
12 | 0.031 | 0.033 | 0.034 | 0.031 | 0.033 | 0.034 | 0.034
13 |  |  |  |  | 0.036 | 0.037 | 0.037
14 |  | 0.032 | 0.031 |  |  | 0.033 | 0.033
15 | 0.031 | 0.03 |  |  |  |  | 0.031
16 | [5 empty] | 0.034 | 0.034
17 | 0.035 | 0.036 | 0.035 | 0.036 |  |  | 0.036
18 | 0.036 |  |  |  | 0.036 | 0.033 | 0.036
19 |  |  |  | 0.034 | 0.035 | 0.037 | 0.037
20 | 0.03 | 0.03 | 0.035 | 0.036 | 0.037 | 0.039 | 0.039
21 | [5 empty] | 0.038 | 0.038
22 | 0.04 | 0.033 | 0.034 | 0.036 | 0.036 |  | 0.038
23 | 0.038 | 0.036 | 0.038 | 0.037 | 0.036 |  | 0.038
24 | [5 empty] | 0.035 | 0.035
25 | 0.038 | 0.037 |  |  | 0.038 | 0.039 | 0.039
26 |  |  | 0.033 | 0.031 |  |  | 0.031
27 | 0.0398 | 0.038 |  |  | 0.031 | 0.033 | 0.038
28 |  |  |  |  | 0.03 | 0.03 | 0.03
29 |  |  | 0.031 | 0.032 | 0.031 | 0.033 | 0.033
30 |  |  |  | 0.031 | 0.036 | 0.036 | 0.036
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:05/10/2021
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2021-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—8 am | 1.02 | 259 | 264.18 | 14.9 | 7.01 | 27.5856 | YES | 7.99
2—8 am | 1 | 259 | 259 | 15.7 | 7.1 | 26.9751 | YES | 5.9
3--8 am | 1 | 259 | 259 | 15.6 | 7.07 | 26.855 | YES | 6.88
4—8 am | 1.03 | 259 | 266.77 | 15.7 | 7 | 26.0791 | YES | 6.32
5—8 am | 1.01 | 259 | 261.59 | 15.7 | 7 | 26.0195 | YES | 6.18
6—9 am | 1.02 | 259 | 264.18 | 15.6 | 7 | 26.2245 | YES | 7.01
7--8 am | 1.02 | 259 | 264.18 | 154.7 | 7 | -0.81302 | YES | 7.01
8--8 am | 1.03 | 259 | 266.77 | 15.8 | 7.01 | 26.0015 | YES | 6.81
9—9 am | 1.02 | 259 | 264.18 | 15.9 | 7.01 | 25.7982 | YES | 7.08
10—8 am | 1.03 | 259 | 266.77 | 16 | 7.02 | 25.7509 | YES | 6.88
11—9 am | 1.04 | 259 | 269.36 | 16.1 | 7.01 | 25.5128 | YES | 8.26
12—9 am | 1.01 | 259 | 261.59 | 16.2 | 7.03 | 25.4442 | YES | 7.64
13—9 am | 1.02 | 259 | 264.18 | 16.3 | 7.02 | 25.2089 | YES | 6.94
14—8 am | 1 | 259 | 259 | 16.8 | 7.01 | 24.2302 | YES | 7.08
15—8 am | 1.02 | 259 | 264.18 | 16.9 | 7.02 | 24.2135 | YES | 8.33
16—8 am | 1.03 | 259 | 266.77 | 16.8 | 7.01 | 24.3138 | YES | 8.4
17—9 am | 1 | 259 | 259 | 16.7 | 7 | 24.3027 | YES | 8.13
18—8 am | 0.99 | 259 | 256.41 | 16.3 | 7.02 | 25.1224 | YES | 7.64
19—8 am | 1 | 259 | 259 | 16.2 | 7.01 | 25.2264 | YES | 7.99
20—9 am | 1.01 | 259 | 261.59 | 16.1 | 7.01 | 25.4253 | YES | 7.5
21—9 am | 1 | 259 | 259 | 17 | 6.99 | 23.7289 | YES | 7.5
22—8 am | 1.03 | 259 | 266.77 | 17.1 | 7 | 23.7397 | YES | 6.88
23—8 am | 1.02 | 259 | 264.18 | 16.7 | 7.01 | 24.4496 | YES | 6.32
24—8 am | 1.03 | 259 | 266.77 | 16.6 | 7.03 | 24.8271 | YES | 7.57
25—8 am | 1.03 | 259 | 266.77 | 16.2 | 7.01 | 25.3132 | YES | 10.07
26—8 am | 1.01 | 259 | 261.59 | 16.3 | 7.01 | 25.0864 | YES | 4.58
27—8 am | 1.04 | 259 | 269.36 | 16.4 | 7.02 | 25.0978 | YES | 7.01
28—9 am | 1 | 259 | 259 | 16.5 | 7.01 | 24.7234 | YES | 7.15
29—8 am | 1.01 | 259 | 261.59 | 16.6 | 7.02 | 24.678 | YES | 9.65
30—8 am | 1.02 | 259 | 264.18 | 16.8 | 7.03 | 24.4678 | YES | 9.51
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2