## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-05-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.028 | 0.031 | 0.033 | 0.033
2 |  |  |  |  | 0.032 | 0.031 | 0.032
3 | 0.032 | 0.031 | 0.031 | 0.03 | 0.034 | 0.034 | 0.034
4 |  |  |  |  | 0.029 | 0.028 | 0.029
5 | 0.029 |  |  |  | 0.03 | 0.031 | 0.031
6 |  |  | 0.032 | 0.033 | 0.034 | 0.035 | 0.035
7 |  |  |  | 0.031 | 0.033 | 0.03 | 0.033
8 | [5 empty] | 0.031 | 0.031
9 |  |  | 0.031 | 0.034 | 0.0321 | 0.032 | 0.034
10 |  |  | 0.034 | 0.034 | 0.033 | 0.03 | 0.034
11 |  |  |  |  | 0.034 | 0.033 | 0.034
12 |  |  |  | 0.301 | 0.032 | 0.03 | 0.032
13 | 0.033 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.034
14 |  |  |  | 0.034 | 0.036 | 0.036 | 0.036
15 |  | 0.038 | 0.038 | 0.038 | 0.039 | 0.035 | 0.039
16 | [5 empty] | 0.04 | 0.04
17 | 0.039 |  | 0.038 |  |  |  | 0.039
18 |  | 0.042 | 0.043 | 0.043 |  |  | 0.043
19 | 0.043 | 0.043 |  |  |  |  | 0.043
20 |  |  |  |  | 0.045 | 0.045 | 0.045
21 |  |  | 0.033 | 0.034 | 0.031 | 0.034 | 0.034
22 |  |  |  |  | 0.03 | 0.031 | 0.031
23 | 0.032 | 0.032 |  |  |  |  | 0.032
24 | 0.03 | 0.031 | 0.032 | 0.03 | 0.03 |  | 0.032
25 | [5 empty] | 0.03 | 0.03
26 | 0.036 |  |  | 0.029 | 0.029 | 0.029 | 0.036
27 |  |  |  | 0.026 | 0.027 | 0.028 | 0.028
28 | 0.028 |  |  |  | 0.029 | 0.028 | 0.029
29 |  |  |  | 0.029 | 0.03 | 0.031 | 0.031
30 | 0.033 | 0.031 | 0.034 |  |  |  | 0.034
31 |  |  | 0.03 | 0.03 | 0.03 | 0.031 | 0.031
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: Amended report. Fixed typo on May 3 “highest reading of the day.” |  |  |  |  | PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:06/10/2021
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2021-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—8 am | 1.01 | 259 | 261.59 | 16.9 | 7.02 | 24.1857 | YES | 9.72
2—8 am | 1.03 | 259 | 266.77 | 16.9 | 7 | 24.061 | YES | 8.47
3--8 am | 1.02 | 259 | 264.18 | 16.7 | 7.02 | 24.541 | YES | 8.4
4—8 am | 1.01 | 259 | 261.59 | 16.8 | 7.03 | 24.4398 | YES | 8.89
5—8 am | 1.02 | 259 | 264.18 | 16.9 | 7.01 | 24.1233 | YES | 8.89
6—8 am | 1.01 | 259 | 261.59 | 16.8 | 7 | 24.1677 | YES | 9.72
7--8 am | 1.02 | 259 | 264.18 | 16.5 | 7 | 24.688 | YES | 6.39
8--8 am | 1.03 | 259 | 266.77 | 16.7 | 7 | 24.3865 | YES | 8.33
9—8 am | 1.04 | 259 | 269.36 | 16.8 | 7.02 | 24.4327 | YES | 10.97
10—8 am | 0.99 | 259 | 256.41 | 16.7 | 7.01 | 24.3656 | YES | 7.85
11—8 am | 0.96 | 259 | 248.64 | 16.6 | 7.01 | 24.4456 | YES | 8.96
12—8 am | 0.94 | 259 | 243.46 | 16.5 | 7.03 | 24.7377 | YES | 7.71
13—8 am | 0.97 | 259 | 251.23 | 17.7 | 7.05 | 23.071 | YES | 7.57
14—8 am | 0.99 | 259 | 256.41 | 17.8 | 7.02 | 22.7128 | YES | 7.57
15—8 am | 1 | 259 | 259 | 17.6 | 7 | 22.8754 | YES | 8.4
16—8 am | 1.03 | 259 | 266.77 | 17.7 | 7.01 | 22.8859 | YES | 7.57
17—9 am | 1.01 | 259 | 261.59 | 17.6 | 7.02 | 23.0736 | YES | 7.5
18—8 am | 1 | 259 | 259 | 17.9 | 7 | 22.4179 | YES | 6.46
19—8 am | 1 | 259 | 259 | 17.7 | 7 | 22.7219 | YES | 8.26
20—8 am | 1.03 | 259 | 266.77 | 17.5 | 7.01 | 23.196 | YES | 7.43
21—8 am | 1.04 | 259 | 269.36 | 17.6 | 7.02 | 23.1533 | YES | 8.54
22—8 am | 1.03 | 259 | 266.77 | 17.3 | 7.03 | 23.6865 | YES | 7.71
23—8 am | 1.02 | 259 | 264.18 | 16.9 | 7.04 | 24.3948 | YES | 9.72
24—8 am | 1.01 | 259 | 261.59 | 16.8 | 7 | 24.1677 | YES | 9.03
25—8 am | 1.02 | 259 | 264.18 | 16.7 | 7.03 | 24.6327 | YES | 7.78
26—8 am | 0.99 | 259 | 256.41 | 17 | 7.01 | 23.8793 | YES | 5.42
27—8 am | 0.98 | 259 | 253.82 | 17.2 | 7 | 23.4456 | YES | 8.33
28—9 am | 1.01 | 259 | 261.59 | 17.3 | 7.02 | 23.544 | YES | 7.64
29—8 am | 1.02 | 259 | 264.18 | 17.3 | 7 | 23.3956 | YES | 8.26
30—8 am | 1.1 | 259 | 284.9 | 17 | 7.04 | 24.4549 | YES | 16.74
31—8 am | 1.02 | 259 | 264.18 | 17.1 | 7.02 | 23.8902 | YES | 8.5
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2