## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-07-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.031 | 0.033 | 0.029 | 0.033
2 | 0.031 |  | 0.032 | 0.033 | 0.038 | 0.036 | 0.038
3 |  |  |  |  | 0.036 | 0.038 | 0.038
4 | 0.039 |  |  | 0.041 | 0.044 | 0.04 | 0.044
5 |  |  | 0.038 | 0.038 |  |  | 0.038
6 | 0.026 | 0.029 | 0.028 | 0.03 | 0.033 | 0.034 | 0.034
7 | 0.029 |  |  | 0.032 | 0.034 | 0.034 | 0.034
8 |  |  | 0.025 | 0.031 | 0.034 | 0.034 | 0.034
9 |  |  | 0.03 | 0.036 | 0.039 | 0.038 | 0.039
10 | 0.033 | 0.032 |  |  |  |  | 0.033
11 | 0.03 | 0.029 | 0.022 |  |  | 0.02 | 0.03
12 |  |  |  | 0.036 | 0.037 | 0.041 | 0.041
13 | 0.037 | 0.035 |  |  |  | 0.031 | 0.037
14 | 0.038 |  |  | 0.039 | 0.041 | 0.04 | 0.041
15 |  |  | 0.03 | 0.038 |  |  | 0.038
16 | 0.036 | 0.035 |  |  | 0.038 | 0.039 | 0.039
17 |  |  |  |  | 0.042 | 0.042 | 0.042
18 | 0.04 | 0.04 |  |  |  | 0.029 | 0.04
19 | 0.03 | 0.029 | 0.034 | 0.038 | 0.031 | 0.036 | 0.038
20 | [5 empty] | 0.031 | 0.031
21 | 0.032 | 0.033 |  |  |  | 0.025 | 0.033
22 |  |  | 0.029 | 0.036 | 0.034 |  | 0.036
23 |  | 0.029 | 0.036 | 0.041 | 0.044 | 0.049 | 0.049
24 |  |  |  |  | 0.03 | 0.033 | 0.033
25 | 0.031 | 0.027 |  |  |  | 0.027 | 0.031
26 | 0.029 | 0.0265 | 0.03 | 0.034 |  |  | 0.034
27 |  |  | 0.029 | 0.038 | 0.041 |  | 0.041
28 |  |  | 0.041 | 0.044 | 0.042 | 0.04 | 0.044
29 | 0.032 |  |  |  | 0.035 | 0.038 | 0.028
30 | 0.033 | 0.029 |  |  | 0.026 | 0.028 | 0.033
31 | 0.026 | 0.026 | 0.03 |  |  |  | 0.03
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: Amended report. Fixed typo on May 3 “highest reading of the day.” |  |  |  |  | PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:08/10/2021
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2021-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—7 am | 1.08 | 259 | 279.72 | 20.1 | 7.03 | 19.7229 | YES | 10.14
2—7 am | 1.07 | 259 | 277.13 | 20 | 7.04 | 19.9086 | YES | 10.56
3—7 am | 1.11 | 259 | 287.49 | 19.4 | 6.99 | 20.4416 | YES | 8.96
4—7 am | 1.05 | 259 | 271.95 | 19.2 | 7.03 | 20.8879 | YES | 6.88
5—7 am | 1.06 | 259 | 274.54 | 18 | 7.05 | 22.8449 | YES | 13.33
6—7 am | 1.03 | 259 | 266.77 | 18.1 | 7 | 22.1943 | YES | 9.86
7—7 am | 1.1 | 259 | 284.9 | 18.2 | 7.03 | 22.4744 | YES | 11.46
8—7 am | 1.09 | 259 | 282.31 | 18.1 | 6.98 | 22.1814 | YES | 10.14
9—7 am | 1.12 | 259 | 290.08 | 18.3 | 7.01 | 22.2081 | YES | 6.94
10—7 am | 1.1 | 259 | 284.9 | 18.6 | 7.03 | 21.8767 | YES | 10.56
11—7 am | 1.08 | 259 | 279.72 | 18.7 | 7.05 | 21.8427 | YES | 12.71
12—7 am | 1.05 | 259 | 271.95 | 18.9 | 7.01 | 21.1561 | YES | 7.01
13—7 am | 1.06 | 259 | 274.54 | 18.6 | 7.04 | 21.8579 | YES | 8.33
14—7 am | 1.04 | 259 | 269.36 | 18.8 | 7.02 | 21.3547 | YES | 9.79
15—7 am | 1.01 | 259 | 261.59 | 18.9 | 7 | 20.9799 | YES | 9.79
16—7 am | 1.08 | 259 | 279.72 | 18.8 | 7.05 | 21.6959 | YES | 9.58
17—7 am | 1.06 | 259 | 274.54 | 18.9 | 7.03 | 21.3399 | YES | 7.29
18—7 am | 1.02 | 259 | 264.18 | 18.8 | 7.07 | 21.7085 | YES | 7.36
19—7 am | 1.05 | 259 | 271.95 | 18.6 | 7.05 | 21.9146 | YES | 15.97
20—7 am | 1.02 | 259 | 264.18 | 18.7 | 7.01 | 21.3696 | YES | 10.56
21—7 am | 1.03 | 259 | 266.77 | 18.8 | 7.04 | 21.4906 | YES | 9.72
22—7 am | 1.09 | 259 | 282.31 | 18.6 | 6.98 | 21.446 | YES | 8.99
23—7 am | 0.99 | 259 | 256.41 | 18.6 | 7.02 | 21.5205 | YES | 9.65
24—7 am | 1.03 | 259 | 266.77 | 18.7 | 7.06 | 21.7988 | YES | 9.17
25—7 am | 1.05 | 259 | 271.95 | 18.6 | 7.08 | 22.1621 | YES | 7.64
26—7 am | 1.09 | 259 | 282.31 | 18.6 | 7.04 | 21.9335 | YES | 9.03
27—7 am | 1.06 | 259 | 274.54 | 17.6 | 7 | 23.0337 | YES | 7.22
28—7 am | 1.03 | 259 | 266.77 | 17.8 | 7.02 | 22.8175 | YES | 7.85
29—7 am | 1 | 259 | 259 | 17.6 | 7.04 | 23.22 | YES | 8.4
30—7 am | 1.01 | 259 | 261.59 | 18 | 7.06 | 22.799 | YES | 9.1
31—7 am | 1.02 | 259 | 264.18 | 18.3 | 7 | 21.8719 | YES | 7.64
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2