## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-02-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.026 | 0.027 |  |  |  |  | 0.027
2 | 0.025 | 0.028 |  |  | 0.026 | 0.026 | 0.028
3 |  |  |  |  | 0.025 | 0.025 | 0.025
4 |  |  | 0.025 | 0.03 | 0.032 |  | 0.03
5 |  |  |  |  | 0.04 | 0.042 | 0.042
6 | 0.044 | 0.046 | 0.048 |  |  |  | 0.048
7 | 0.05 | 0.053 | 0.051 |  |  |  | 0.053
8 |  |  |  | 0.046 | 0.048 | 0.044 | 0.048
9 | 0.051 | 0.05 |  |  | 0.047 | 0.047 | 0.051
10 | 0.047 |  |  | 0.042 | 0.044 | 0.044 | 0.047
11 |  |  | 0.052 | 0.054 |  |  | 0.054
12 |  | 0.046 | 0.046 | 0.049 | 0.047 | 0.047 | 0.049
13 |  |  |  |  | 0.033 | 0.038 | 0.038
14 | 0.033 | 0.035 |  |  | 0.042 | 0.042 | 0.042
15 |  |  | 0.035 | 0.04 | 0.043 |  | 0.043
16 |  | 0.048 | 0.042 | 0.046 | 0.053 |  | 0.053
17 |  |  |  | 0.051 | 0.046 | 0.048 | 0.051
18 | 0.053 |  |  |  |  | 0.039 | 0.053
19 | 0.041 | 0.036 | 0.038 |  |  |  | 0.041
20 | 0.055 | 0.053 | 0.057 | 0.055 |  |  | 0.057
21 |  |  | 0.053 | 0.059 | 0.062 | 0.06 | 0.062
22 |  |  |  | 0.054 | 0.057 | 0.055 | 0.057
23 | 0.048 | 0.044 |  |  |  | 0.047 | 0.048
24 | 0.044 | 0.052 | 0.059 |  |  |  | 0.059
25 | 0.061 | 0.06 | 0.064 | 0.064 | 0.068 |  | 0.068
26 |  |  | 0.073 | 0.075 | 0.077 | 0.072 | 0.077
27 |  |  | 0.068 | 0.069 | 0.066 | 0.064 | 0.069
28 |  |  |  | 0.058 | 0.058 | 0.062 | 0.062
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:03/10/2022
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2022-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—8 am | 0.77 | 259 | 199.43 | 10 | 7.02 | 37.879 | YES | 9.38
2—8 am | 0.75 | 259 | 194.25 | 10.3 | 7 | 36.8137 | YES | 10.35
3—9 am | 0.8 | 259 | 207.2 | 10.6 | 7.03 | 36.6843 | YES | 10.28
4—9 am | 0.81 | 259 | 209.79 | 10.5 | 7.02 | 36.8359 | YES | 9.31
5—1423 | 0.83 | 259 | 214.97 | 10.6 | 7.01 | 36.5538 | YES | 12.36
6—8 am | 0.8 | 259 | 207.2 | 10.8 | 7 | 35.843 | YES | 8.4
7—8 am | 0.85 | 259 | 220.15 | 10.6 | 6.98 | 36.2588 | YES | 9.65
8—8 am | 0.83 | 259 | 214.97 | 10.4 | 6.96 | 36.3975 | YES | 11.04
9—8 am | 0.79 | 259 | 204.61 | 10.7 | 7 | 36.0348 | YES | 11.67
10—6 am | 0.76 | 259 | 196.84 | 11 | 7.03 | 35.5934 | YES | 9.44
11—6 am | 0.78 | 259 | 202.02 | 11.2 | 7.06 | 35.5799 | YES | 10.49
12—6 am | 0.8 | 259 | 207.2 | 11.4 | 7.01 | 34.6065 | YES | 10.21
13—6 am | 0.83 | 259 | 214.97 | 11.2 | 7.03 | 35.4105 | YES | 7.57
14—6 am | 0.81 | 259 | 209.79 | 11.1 | 7.01 | 35.3178 | YES | 11.94
15—6 am | 0.86 | 259 | 222.74 | 11.3 | 7 | 34.9397 | YES | 10.97
16—6 am | 0.88 | 259 | 227.92 | 11.5 | 7.04 | 35.0461 | YES | 10.56
17—6 am | 0.85 | 259 | 220.15 | 11.7 | 7.01 | 34.135 | YES | 10
18—6 am | 0.81 | 259 | 209.79 | 11.6 | 7 | 34.0875 | YES | 9.38
19—6 am | 0.83 | 259 | 214.97 | 11.3 | 7.03 | 35.1838 | YES | 11.6
20—6 am | 0.79 | 259 | 204.61 | 10.1 | 7.01 | 37.588 | YES | 14.51
21—6 am | 0.76 | 259 | 196.84 | 10 | 6.99 | 37.4472 | YES | 7.08
22—6 am | 0.74 | 259 | 191.66 | 10.2 | 6.97 | 36.6311 | YES | 8.13
23—6 am | 0.76 | 259 | 196.84 | 10.1 | 6.96 | 36.8231 | YES | 10.21
24—6 am | 0.69 | 259 | 178.71 | 10.3 | 6.95 | 35.9475 | YES | 10.07
25—6 am | 0.7 | 259 | 181.3 | 10.2 | 6.93 | 35.9719 | YES | 10.07
26—6 am | 0.73 | 259 | 189.07 | 10.1 | 6.9 | 35.9523 | YES | 10.97
27—6 am | 0.74 | 259 | 191.66 | 10 | 6.94 | 36.7262 | YES | 12.92
28—6 am | 0.76 | 259 | 196.84 | 10 | 6.91 | 36.4296 | YES | 7.52
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2