## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-03-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  |  | 0.026 | 0.029 | 0.029
2 | 0.028 | 0.033 | 0.03 |  |  |  | 0.033
3 | 0.029 | 0.026 | 0.027 | 0.028 | 0.027 |  | 0.029
4 |  |  |  |  | 0.04 | 0.043 | 0.043
5 | 0.035 | 0.036 | 0.033 |  |  |  | 0.036
6 | 0.037 | 0.033 | 0.036 | 0.03 | 0.031 |  | 0.037
7 | [5 empty] | 0.027 | 0.027
8 | 0.028 | 0.026 | 0.027 | 0.026 |  |  | 0.028
9 |  |  |  | 0.03 | 0.031 | 0.032 | 0.032
10 | 0.033 | 0.032 | 0.036 | 0.032 |  |  | 0.033
11 |  |  |  |  | 0.026 | 0.025 | 0.026
12 | 0.028 | 0.027 | 0.025 | 0.028 |  |  | 0.028
13 |  |  |  |  | 0.027 | 0.028 | 0.03
14 | 0.04 | 0.039 | 0.036 | 0.041 | 0.042 |  | 0.042
15 |  |  |  |  | 0.036 | 0.037 | 0.036
16 | 0.031 | 0.032 |  |  |  |  | 0.032
17 | 0.0298 | 0.028 | 0.027 | 0.029 | 0.029 | 0.03 | 0.03
18 | 0.027 | [5 empty] | 0.027
19 | 0.026 | 0.025 | 0.027 | 0.025 |  |  | 0.027
20 | 0.029 | 0.041 |  |  |  | 0.042 | 0.042
21 |  |  |  | 0.04 | 0.047 | 0.043 | 0.043
22 | 0.04 | 0.037 | 0.029 | 0.03 | 0.032 | 0.03 | 0.04
23 | [5 empty] | 0.033 | 0.033
24 | 0.035 | 0.034 |  |  | 0.036 | 0.035 | 0.036
25 |  |  |  |  | 0.038 | 0.036 | 0.038
26 | 0.03 | 0.028 | 0.026 | 0.025 |  |  | 0.03
27 |  |  |  | 0.033 | 0.034 | 0.029 | 0.034
28 | 0.025 | 0.027 | 0.029 | 0.026 |  |  | 0.029
29 |  |  |  | 0.027 | 0.029 | 0.027 | 0.029
30 |  |  | 0.025 | 0.026 | 0.027 |  | 0.027
31 |  | 0.025 |  |  |  | 0.025 | 0.025
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:04/09/2022
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2022-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—6 am | 0.93 | 58 | 53.94 | 10.1 | 7.11 | 39.5229 | YES | 10
2—6 am | 0.89 | 58 | 51.62 | 10.2 | 7.12 | 39.2274 | YES | 8.47
3—6 am | 0.86 | 58 | 49.88 | 10 | 7.12 | 39.6091 | YES | 10.56
4—6 am | 0.84 | 58 | 48.72 | 10 | 7.1 | 39.2474 | YES | 10.07
5—6 am | 0.8 | 58 | 46.4 | 10.3 | 7.11 | 38.451 | YES | 10.21
6—6 am | 0.79 | 58 | 45.82 | 10.2 | 7.1 | 38.525 | YES | 11.11
7—6 am | 0.76 | 58 | 44.08 | 10.1 | 7.13 | 39.0508 | YES | 7.78
8—6 am | 0.74 | 58 | 42.92 | 10.3 | 7.15 | 38.7279 | YES | 10
9—6 am | 0.72 | 58 | 41.76 | 10.1 | 7.16 | 39.2838 | YES | 9.38
10—6 am | 0.7 | 58 | 40.6 | 10.2 | 7.13 | 38.5394 | YES | 9.72
11—6 am | 0.72 | 58 | 41.76 | 10.3 | 7.1 | 37.9791 | YES | 10
12—6 am | 0.75 | 58 | 43.5 | 10 | 7.08 | 38.5875 | YES | 10.76
13—6 am | 0.77 | 58 | 44.66 | 10.3 | 7.06 | 37.6664 | YES | 11.18
14—6 am | 0.68 | 58 | 39.44 | 10.1 | 6.95 | 36.3737 | YES | 7.64
15—6 am | 0.73 | 58 | 42.34 | 10.4 | 6.91 | 35.3862 | YES | 9.58
16—6 am | 0.78 | 58 | 45.24 | 10.2 | 6.93 | 36.2909 | YES | 9.31
17—6 am | 0.8 | 58 | 46.4 | 10.1 | 6.9 | 36.231 | YES | 7.71
18—6 am | 0.78 | 58 | 45.24 | 10.3 | 6.94 | 36.1817 | YES | 11.88
19—6 am | 0.83 | 58 | 48.14 | 10.2 | 6.96 | 36.8704 | YES | 10.49
20—6 am | 0.8 | 58 | 46.4 | 10.3 | 6.97 | 36.6376 | YES | 12.29
21—6 am | 0.83 | 58 | 48.14 | 10.2 | 6.95 | 36.7437 | YES | 9.03
22—6 am | 0.85 | 58 | 49.3 | 10 | 6.93 | 37.0481 | YES | 10.63
23—6 am | 0.88 | 58 | 51.04 | 10.3 | 6.97 | 36.9632 | YES | 9.65
24—6 am | 0.9 | 58 | 52.2 | 10.4 | 6.98 | 36.9335 | YES | 7.5
25—6 am | 0.92 | 58 | 53.36 | 10.2 | 7 | 37.7571 | YES | 11.11
26—6 am | 0.85 | 58 | 49.3 | 10.4 | 7.01 | 37.1112 | YES | 7.71
27—6 am | 0.81 | 58 | 46.98 | 10.5 | 7.02 | 36.8359 | YES | 7.99
28—6 am | 0.79 | 58 | 45.82 | 10.6 | 7 | 36.2678 | YES | 11.25
29—6 am | 0.76 | 58 | 44.08 | 10.7 | 7.01 | 36.0393 | YES | 15.83
30—6 am | 0.78 | 58 | 45.24 | 10.5 | 7 | 36.4622 | YES | 7.64
31—6 am | 0.77 | 58 | 44.66 | 10.6 | 6.99 | 36.0638 | YES | 5.97
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2