## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-04-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  |  | 0.033 | 0.036 | 0.036
2 | 0.03 | 0.031 | 0.033 |  |  |  | 0.033
3 | 0.031 | 0.03 | 0.029 | 0.026 |  |  | 0.031
4 | 0.029 | 0.027 |  |  |  |  | 0.029
5 | 0.027 | 0.025 | 0.025 | 0.026 |  |  | 0.027
6 | [5 empty] | 0.029 | 0.029
7 | 0.037 | 0.04 | 0.042 | 0.04 | 0.042 |  | 0.042
8 |  |  |  | 0.03 | 0.033 | 0.035 | 0.035
9 | 0.029 | 0.028 |  |  |  |  | 0.029
10 | 0.025 | 0.025 | 0.027 | 0.026 |  |  | 0.027
11 | 0.028 | 0.025 | 0.027 |  |  |  | 0.028
12 | 0.039 | 0.043 | 0.04 | 0.044 |  |  | 0.044
13 |  |  |  |  | 0.041 | 0.042 | 0.042
14 | 0.04 | 0.046 | 0.047 |  |  |  | 0.047
15 | 0.027 | 0.025 | 0.026 |  |  |  | 0.027
16 | 0.03 | 0.032 | 0.033 | 0.031 | 0.032 |  | 0.033
17 | [5 empty] | 0.03 | 0.03
18 | 0.031 | 0.032 | 0.03 |  |  |  | 0.031
19 | 0.029 | 0.027 | 0.025 | 0.027 |  |  | 0.029
20 | 0.025 | [5 empty] | 0.025
21 | 0.026 | 0.028 | 0.027 | 0.026 | 0.029 | 0.026 | 0.029
22 | 0.031 | 0.03 |  |  |  |  | 0.031
23 | 0.032 | 0.035 | 0.037 | 0.035 | 0.037 |  | 0.037
24 | 0.039 | 0.036 |  |  |  | 0.037 | 0.039
25 |  |  |  | 0.04 | 0.042 | 0.044 | 0.044
26 |  |  |  | 0.038 | 0.036 | 0.033 | 0.0387
27 | 0.032 | 0.031 |  |  |  |  | 0.032
28 | 0.028 | 0.025 | 0.026 | 0.027 |  |  | 0.027
29 | 0.029 | 0.026 | 0.025 | 0.025 | 0.029 |  | 0.029
30 |  |  |  |  | 0.026 | 0.025 | 0.026
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:05/09/2022
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2022-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—6 am | 0.78 | 58 | 45.24 | 12.1 | 6.91 | 31.9235 | YES | 14.1
2—6 am | 0.72 | 58 | 41.76 | 12 | 6.94 | 32.2428 | YES | 8.06
3—6 am | 0.8 | 58 | 46.4 | 12.3 | 6.96 | 32.1277 | YES | 13.54
4—6 am | 0.82 | 58 | 47.56 | 12.5 | 6.98 | 31.302 | YES | 8.82
5—6 am | 0.84 | 58 | 48.72 | 12.3 | 6.97 | 32.3767 | YES | 9.72
6—6 am | 0.8 | 58 | 46.4 | 12.1 | 6.95 | 32.428 | YES | 9.44
7—6 am | 0.82 | 58 | 47.56 | 12.2 | 6.97 | 32.5121 | YES | 10.35
8—6 am | 0.84 | 58 | 48.72 | 12.4 | 6.96 | 32.0636 | YES | 9.44
9—6 am | 0.82 | 58 | 47.56 | 12.3 | 7 | 32.6359 | YES | 7.15
10—6 am | 0.87 | 58 | 50.46 | 11.9 | 7.02 | 33.8905 | YES | 14.31
11—6 am | 0.85 | 58 | 49.3 | 11.7 | 7 | 34.0189 | YES | 8.68
12—6 am | 0.87 | 58 | 50.46 | 11.8 | 7.02 | 34.1078 | YES | 10.35
13—6 am | 0.86 | 58 | 49.88 | 11.6 | 7.01 | 34.3917 | YES | 9.86
14—6 am | 0.88 | 58 | 51.04 | 11.4 | 7 | 34.7926 | YES | 10.28
15—6 am | 0.89 | 58 | 51.62 | 11.6 | 7.03 | 34.7414 | YES | 9.65
16—6 am | 0.9 | 58 | 52.2 | 10.8 | 7.01 | 36.3653 | YES | 10
17—6 am | 0.92 | 58 | 53.36 | 10.7 | 7 | 36.5557 | YES | 5.35
18—6 am | 0.91 | 58 | 52.78 | 10.2 | 7.03 | 38.1082 | YES | 14.65
19—6 am | 0.89 | 58 | 51.62 | 10.1 | 7 | 37.8763 | YES | 9.24
20—6 am | 0.88 | 58 | 51.04 | 10 | 7.02 | 38.3448 | YES | 10.21
21—6 am | 0.83 | 58 | 48.14 | 10.3 | 7.01 | 37.2693 | YES | 9.79
22—6 am | 0.84 | 58 | 48.72 | 10.6 | 7 | 36.4686 | YES | 9.72
23—6 am | 0.86 | 58 | 49.88 | 10.87 | 7.02 | 36.1661 | YES | 7.71
24—6 am | 0.89 | 58 | 51.62 | 10.4 | 7 | 37.1477 | YES | 12.85
25—6 am | 0.81 | 58 | 46.98 | 10.5 | 7 | 36.5832 | YES | 9.51
26—6 am | 0.83 | 58 | 48.14 | 10.9 | 7.02 | 35.977 | YES | 10.14
27—6 am | 0.9 | 58 | 52.2 | 10.4 | 6.98 | 36.9335 | YES | 10.14
28—6 am | 0.96 | 58 | 55.68 | 10.6 | 7 | 36.9557 | YES | 9.72
29—6 am | 0.97 | 58 | 56.26 | 10.8 | 7.01 | 36.6477 | YES | 12.78
30—6 am | 0.95 | 58 | 55.1 | 10.7 | 7.02 | 36.9305 | YES | 7.36
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2