## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-06-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.04 | 0.041 |  |  |  |  | 0.041
2 | 0.043 | 0.043 | 0.043 | 0.043 |  |  | 0.043
3 |  | 0.042 | 0.042 |  |  |  | 0.042
4 |  | 0.04 | 0.041 | 0.041 |  |  | 0.041
5 | 0.042 | 0.042 | 0.04 |  |  |  | 0.042
6 | 0.043 | 0.043 | 0.044 |  |  |  | 0.044
7 | 0.043 | 0.043 | 0.046 | 0.047 |  |  | 0.047
8 | 0.045 | 0.045 |  |  |  |  | 0.045
9 |  | 0.044 | 0.047 | 0.048 |  |  | 0.048
10 | 0.041 | 0.041 | 0.05 | 0.049 | 0.048 |  | 0.05
11 | 0.04 | 0.04 | 0.045 | 0.047 | 0.046 | 0.043 | 0.047
12 | 0.041 | 0.042 |  |  |  |  | 0.042
13 | 0.04 | 0.04 | 0.044 |  |  |  | 0.044
14 | 0.043 | 0.043 | 0.045 | 0.043 |  |  | 0.045
15 | 0.044 | 0.046 |  |  |  |  | 0.046
16 | 0.046 | 0.048 | 0.047 | 0.05 | 0.051 |  | 0.051
17 | 0.049 | 0.05 |  |  |  |  | 0.05
18 | 0.049 | 0.05 | 0.049 | 0.053 | 0.05 | 0.05 | 0.053
19 | 0.051 | 0.051 | 0.051 | 0.049 | 0.049 | 0.049 | 0.051
20 | 0.049 | 0.049 | 0.049 | 0.049 | 0.05 | 0.05 | 0.05
21 | 0.05 | 0.05 | 0.048 | 0.049 | 0.048 | 0.05 | 0.05
22 | 0.049 | 0.049 | 0.048 | 0.048 | 0.048 | 0.048 | 0.049
23 | 0.051 | 0.051 | 0.051 | 0.051 | 0.049 | 0.049 | 0.051
24 | 0.049 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
25 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.051 | 0.051
26 | 0.05 | 0.05 | 0.05 | 0.05 | 0.049 | 0.049 | 0.05
27 | 0.049 | 0.049 | 0.05 | 0.051 | 0.052 | 0.051 | 0.052
28 | 0.051 | 0.052 | 0.051 | 0.05 | 0.05 | 0.051 | 0.051
29 | 0.051 | 0.051 | 0.048 | 0.049 | 0.049 | 0.05 | 0.051
30 | 0.05 | 0.05 | 0.051 | 0.05 | 0.052 | 0.051 | 0.052
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:07/09/2022
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2022-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—6 am | 0.99 | 58 | 57.42 | 18.6 | 7 | 21.3598 | YES | 10.69
2—6 am | 0.96 | 58 | 55.68 | 18.5 | 7 | 21.4302 | YES | 9.58
3—6 am | 0.98 | 58 | 56.84 | 18.6 | 7.03 | 21.5764 | YES | 9.79
4—6 am | 0.94 | 58 | 54.52 | 18.9 | 7.01 | 20.8894 | YES | 11.11
5—6 am | 0.92 | 58 | 53.36 | 19.2 | 7.02 | 20.4999 | YES | 11.11
6—6 am | 0.9 | 58 | 52.2 | 19.3 | 7 | 20.1628 | YES | 6.32
7—6 am | 0.89 | 58 | 51.62 | 19.1 | 6.96 | 20.1094 | YES | 10.56
8—6 am | 0.91 | 58 | 52.78 | 18.6 | 6.92 | 20.5381 | YES | 11.39
9—6 am | 0.93 | 58 | 53.94 | 18.3 | 6.94 | 21.1651 | YES | 10.35
10—6 am | 0.88 | 58 | 51.04 | 18.6 | 6.95 | 20.6988 | YES | 13.68
11—6 am | 0.86 | 58 | 49.88 | 18.2 | 6.94 | 21.1372 | YES | 8.75
12—6 am | 0.84 | 58 | 48.72 | 18.4 | 6.95 | 20.8838 | YES | 8.75
13—6 am | 0.82 | 58 | 47.56 | 18.6 | 6.97 | 20.7109 | YES | 7.71
14—6 am | 0.8 | 58 | 46.4 | 18.8 | 6.99 | 20.5394 | YES | 12.71
15—6 am | 0.82 | 58 | 47.56 | 18.5 | 7 | 21.0872 | YES | 9.51
16—6 am | 0.85 | 58 | 49.3 | 18.9 | 7.02 | 20.7514 | YES | 9.86
17—6 am | 0.83 | 58 | 48.14 | 19 | 7 | 20.4103 | YES | 10.07
18—6 am | 0.87 | 58 | 50.46 | 19.2 | 7.01 | 20.3055 | YES | 10.49
19—6 am | 0.83 | 58 | 48.14 | 19.4 | 7.02 | 20.0154 | YES | 12.43
20—6 am | 0.86 | 58 | 49.88 | 19.5 | 7 | 19.8001 | YES | 6.46
21—6 am | 0.89 | 58 | 51.62 | 19.7 | 7.03 | 19.824 | YES | 9.93
22—6 am | 0.91 | 58 | 52.78 | 19.9 | 7 | 19.3828 | YES | 9.51
23—6 am | 0.93 | 58 | 53.94 | 20.3 | 7.05 | 19.2674 | YES | 9.49
24—6 am | 0.95 | 58 | 55.1 | 20.2 | 7.06 | 19.5165 | YES | 11.25
25—6 am | 0.93 | 58 | 53.94 | 20 | 7.05 | 19.6628 | YES | 11.32
26—6 am | 0.9 | 58 | 52.2 | 20.1 | 7.03 | 19.3166 | YES | 11.39
27—6 am | 0.93 | 58 | 53.94 | 20 | 7 | 19.2965 | YES | 9.86
28—6 am | 0.89 | 58 | 51.62 | 19.6 | 6.98 | 19.587 | YES | 9.93
29—6 am | 0.88 | 58 | 51.04 | 19.5 | 6.99 | 19.7715 | YES | 11.25
30—6 am | 0.86 | 58 | 49.88 | 19.4 | 7.01 | 20.0096 | YES | 9.79
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2