## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-10-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.042 | 0.043 |  |  |  | 0.043
2 | 0.04 | 0.044 | 0.046 | 0.049 |  |  | 0.049
3 | 0.038 | 0.036 | 0.034 |  |  |  | 0.038
4 | 0.044 | 0.041 | 0.047 |  | 0.042 |  | 0.047
5 | 0.035 | 0.037 | 0.034 |  |  | 0.031 | 0.037
6 | 0.03 | 0.033 | 0.031 |  |  |  | 0.033
7 |  | 0.03 | 0.033 | 0.035 |  |  | 0.035
8 |  | 0.028 | 0.026 |  |  |  | 0.028
9 |  | 0.035 | 0.038 | 0.037 | 0.041 |  | 0.041
10 |  | 0.031 | 0.033 |  |  |  | 0.033
11 | 0.05 | 0.05 | 0.053 | 0.054 |  |  | 0.054
12 | 0.046 | 0.048 |  |  |  |  | 0.048
13 | 0.05 | 0.052 | 0.055 |  |  |  | 0.055
14 | 0.049 | 0.05 | 0.047 |  |  |  | 0.05
15 | 0.05 | 0.055 |  |  |  |  | 0.055
16 | 0.052 | 0.058 | 0.05 | 0.055 |  |  | 0.058
17 | 0.046 | 0.049 | 0.042 |  |  |  | 0.049
18 | 0.041 | 0.045 | 0.044 | 0.04 |  |  | 0.045
19 |  | 0.04 | 0.046 | 0.041 | 0.048 |  | 0.048
20 | 0.036 | 0.039 | 0.034 |  |  |  | 0.039
21 | 0.033 | 0.036 | 0.037 | 0.035 |  |  | 0.037
22 | 0.031 | 0.034 | 0.03 | 0.031 |  |  | 0.034
23 | 0.039 | 0.043 | 0.038 |  |  |  | 0.043
24 | 0.05 | 0.051 | 0.055 | 0.053 |  |  | 0.055
25 |  | 0.054 | 0.056 | 0.058 |  |  | 0.058
26 | 0.053 | 0.058 | 0.057 | 0.059 |  |  | 0.059
27 | 0.051 | 0.05 | 0.054 | 0.055 | 0.056 |  | 0.056
28 | 0.052 | 0.055 | 0.058 | 0.06 |  |  | 0.06
29 | 0.054 | 0.053 |  |  |  |  | 0.054
30 | 0.047 | 0.049 | 0.045 |  |  |  | 0.049
31 | 0.044 | 0.041 |  |  |  |  | 0.044
Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
PRINTED NAME: Michael Murphy
[5 empty] | SIGNATURE: Electronic submission |  |  | DATE:11/09/2022
[5 empty] | PHONE #: ( 541 ) 253-6191 |  |  | CERT #: T-09453
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : A
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2022-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1—0600 | 0.89 | 58 | 51.62 | 13.1 | 7 | 30.54 | YES | 10.83
2—0600 | 0.88 | 58 | 51.04 | 12.9 | 7.01 | 31.0298 | YES | 8.82
3—0600 | 0.94 | 58 | 54.52 | 12.2 | 7 | 33.2763 | YES | 2.36
4—0600 | 0.91 | 58 | 52.78 | 12.1 | 7.01 | 33.4932 | YES | 4.51
5—0600 | 0.89 | 58 | 51.62 | 12.2 | 7.04 | 33.5479 | YES | 4.65
6—0600 | 0.86 | 58 | 49.88 | 12.4 | 7.01 | 32.6811 | YES | 4.23
7—0600 | 1.03 | 58 | 59.74 | 12.6 | 6.99 | 31.9646 | YES | 4.93
8—0600 | 1.01 | 58 | 58.58 | 12.1 | 6.96 | 33.2906 | YES | 4.23
9—0600 | 1 | 58 | 58 | 12 | 6.95 | 33.3534 | YES | 4.58
10—0600 | 1.02 | 58 | 59.16 | 12.3 | 6.97 | 33.017 | YES | 3.95
11—0600 | 1.03 | 58 | 59.74 | 12.5 | 6.99 | 32.1783 | YES | 4.44
12—0600 | 1 | 58 | 58 | 12 | 7.01 | 34.0409 | YES | 5.06
13—0600 | 1.01 | 58 | 58.58 | 12.3 | 7 | 33.3185 | YES | 5.41
14—0600 | 1 | 58 | 58 | 12.5 | 6.97 | 31.8321 | YES | 4.09
15—0600 | 0.86 | 58 | 49.88 | 12.6 | 6.95 | 30.8906 | YES | 2.15
16—0600 | 0.81 | 58 | 46.98 | 12.7 | 6.97 | 30.7379 | YES | 2.15
17—0600 | 0.77 | 58 | 44.66 | 13.1 | 6.98 | 29.9025 | YES | 5.41
18—0600 | 0.7 | 58 | 40.6 | 13.3 | 6.91 | 28.5203 | YES | 4.02
19—0600 | 0.76 | 58 | 44.08 | 13.1 | 6.93 | 29.3195 | YES | 5.13
20—0600 | 0.78 | 58 | 45.24 | 13.2 | 6.96 | 29.5176 | YES | 4.72
21—0600 | 0.9 | 58 | 52.2 | 13.4 | 6.9 | 28.8771 | YES | 4.51
22—0600 | 0.92 | 58 | 53.36 | 13.6 | 6.97 | 29.3105 | YES | 5.31
23—0600 | 0.96 | 58 | 55.68 | 13.3 | 6.93 | 29.5981 | YES | 6.94
24—0600 | 0.9 | 58 | 52.2 | 13.1 | 6.96 | 30.1248 | YES | 4.38
25—0600 | 0.96 | 58 | 55.68 | 13.2 | 7 | 30.5798 | YES | 2.98
26—0600 | 0.98 | 58 | 56.84 | 13 | 7.04 | 31.525 | YES | 3.95
27—0600 | 1 | 58 | 58 | 13.2 | 7.06 | 31.4101 | YES | 2.22
28—0600 | 1.01 | 58 | 58.58 | 13.4 | 7.07 | 31.1443 | YES | 2.22
29—0600 | 1.03 | 58 | 59.74 | 13.6 | 7.03 | 30.3484 | YES | 5
30—0600 | 1.01 | 58 | 58.58 | 13.4 | 7.01 | 30.4595 | YES | 6.31
31—0600 | 1.02 | 58 | 59.16 | 13.2 | 7.02 | 31.0187 | YES | 3.47
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours.
PAGE 2 of 2