## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-12-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.041 | 0.039 | 0.037 |  |  | 0.041
2 |  | 0.037 | 0.036 | 0.038 |  |  | 0.038
3 | 0.035 | 0.039 | 0.042 | 0.044 |  |  | 0.042
4 | 0.038 | 0.035 | 0.038 |  |  | 0.038 | 0.038
5 |  |  | 0.037 | 0.036 |  |  | 0.037
6 | 0.048 | 0.049 | 0.046 |  |  |  | 0.049
7 | 0.035 | 0.036 | 0.033 |  |  | 0.035 | 0.036
8 | 0.036 | 0.039 | 0.04 |  |  | 0.044 | 0.044
9 |  |  | 0.043 |  | 0.04 |  | 0.043
10 |  | 0.041 | 0.044 | 0.047 | 0.044 |  | 0.047
11 |  |  | 0.046 | 0.044 |  | 0.049 | 0.049
12 | 0.05 | 0.053 | 0.055 |  |  |  | 0.055
13 | 0.052 | 0.053 | 0.05 |  |  |  | 0.053
14 |  |  | 0.057 | 0.054 | 0.053 | 0.051 | 0.057
15 | 0.056 | 0.055 | 0.058 |  |  |  | 0.058
16 | 0.05 | 0.051 | 0.05 |  |  |  | 0.051
17 | 0.046 | 0.049 | 0.042 |  |  |  | 0.049
18 | 0.041 | 0.045 | 0.044 | 0.041 |  |  | 0.044
19 |  | 0.04 | 0.046 | 0.043 |  | 0.042 | 0.046
20 | 0.037 | 0.035 | 0.037 |  |  |  | 0.037
21 | 0.035 | 0.038 | 0.039 |  |  | 0.036 | 0.039
22 | 0.032 | 0.032 | 0.034 |  | 0.036 | 0.04 | 0.04
23 |  |  | 0.039 |  | 0.048 | 0.047 | 0.048
24 | 0.03 | 0.033 | 0.036 |  |  |  | 0.036
25 | 0.031 | 0.037 | 0.032 |  | 0.041 | 0.042 | 0.042
26 | 0.04 | 0.043 | 0.045 |  |  |  | 0.045
27 | 0.031 | 0.032 | 0.035 |  |  |  | 0.035
28 | 0.04 | 0.041 | 0.038 | 0.036 |  |  | 0.041
29 |  |  | 0.033 | 0.038 | 0.032 |  | 0.038
30 | 0.031 | 0.036 | 0.034 |  |  |  | 0.036
31 | 0.047 | 0.043 | 0.041 |  |  |  | 0.047
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 01-06-23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT#:T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: 12/2022 |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.88 | 58 | 51.04 | 10.9 | 7.02 | 36.176 | YES | 5.07
2 | 0.86 | 58 | 49.88 | 10.7 | 7.01 | 36.4393 | YES | 4.79
3 | 0.9 | 58 | 52.2 | 10.4 | 7 | 37.1888 | YES | 6.6
4 | 0.92 | 58 | 53.36 | 10.2 | 7.02 | 38.0189 | YES | 4.65
5 | 0.94 | 58 | 54.52 | 10.4 | 6.99 | 37.2254 | YES | 3.26
6 | 0.95 | 58 | 55.1 | 10.6 | 6.97 | 36.5357 | YES | 4.58
7 | 0.97 | 58 | 56.26 | 10.5 | 6.95 | 36.601 | YES | 4.51
8 | 1.01 | 58 | 58.58 | 10.3 | 6.94 | 37.1135 | YES | 4.72
9 | 1.02 | 58 | 59.16 | 10.2 | 6.92 | 37.1388 | YES | 4.51
10 | 1 | 58 | 58 | 10.1 | 6.94 | 37.5553 | YES | 3.82
11 | 1.02 | 58 | 59.16 | 10.4 | 6.99 | 37.557 | YES | 7.36
12 | 1.01 | 58 | 58.58 | 10.3 | 6.95 | 37.2416 | YES | 2.85
13 | 1.02 | 58 | 59.16 | 10.2 | 7 | 38.1787 | YES | 4.38
14 | 0.98 | 58 | 56.84 | 10.1 | 7.02 | 38.5226 | YES | 6.11
15 | 0.96 | 58 | 55.68 | 10.1 | 7.01 | 38.3042 | YES | 3.13
16 | 0.89 | 58 | 51.62 | 10.2 | 7 | 37.6317 | YES | 4.51
17 | 0.88 | 58 | 51.04 | 10.3 | 7.02 | 37.606 | YES | 5.07
18 | 0.86 | 58 | 49.88 | 10.5 | 7 | 36.786 | YES | 6.6
19 | 0.87 | 58 | 50.46 | 10.7 | 7.01 | 36.4796 | YES | 3.75
20 | 0.85 | 58 | 49.3 | 10.4 | 6.98 | 36.7298 | YES | 5.76
21 | 0.84 | 58 | 48.72 | 10.3 | 6.96 | 36.6736 | YES | 6.53
22 | 0.9 | 58 | 52.2 | 10.1 | 6.99 | 37.7876 | YES | 1.6
23 | 0.93 | 58 | 53.94 | 10.4 | 6.93 | 36.4242 | YES | 5.63
24 | 0.9 | 58 | 52.2 | 10.2 | 6.96 | 37.1572 | YES | 7.36
25 | 0.95 | 58 | 55.1 | 10.1 | 6.95 | 37.4767 | YES | 1.94
26 | 0.97 | 58 | 56.26 | 10.3 | 6.97 | 37.3335 | YES | 4.44
27 | 0.95 | 58 | 55.1 | 10.5 | 6.93 | 36.27 | YES | 4.44
28 | 0.94 | 58 | 54.52 | 10.3 | 6.95 | 36.9541 | YES | 6.11
29 | 0.91 | 58 | 52.78 | 10.5 | 6.93 | 36.1103 | YES | 4.24
30 | 0.9 | 58 | 52.2 | 10.4 | 6.96 | 36.6801 | YES | 6.04
31 | 0.88 | 58 | 51.04 | 10.7 | 6.99 | 36.2697 | YES | 4.58
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2