## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-03-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.04 | 0.043 |  |  | 0.041 | 0.043
2 | 0.042 | 0.046 | 0.047 | 0.045 |  |  | 0.047
3 | 0.03 | 0.033 | 0.035 |  |  |  | 0.035
4 | 0.044 | 0.041 | 0.047 |  | 0.042 |  | 0.047
5 | 0.035 | 0.037 | 0.034 |  |  | 0.031 | 0.037
6 | 0.03 | 0.033 | 0.031 |  |  |  | 0.033
7 |  | 0.03 | 0.033 | 0.035 |  |  | 0.035
8 |  | 0.028 | 0.026 |  |  |  | 0.028
9 |  | 0.035 | 0.038 | 0.037 | 0.041 |  | 0.041
10 |  | 0.031 | 0.033 |  |  |  | 0.033
11 | 0.05 | 0.05 | 0.053 | 0.054 |  |  | 0.054
12 | 0.046 | 0.048 |  |  |  |  | 0.048
13 | 0.05 | 0.052 | 0.055 |  |  |  | 0.055
14 | 0.049 | 0.05 | 0.047 |  |  |  | 0.05
15 | 0.05 | 0.055 |  |  |  |  | 0.055
16 | 0.052 | 0.058 | 0.05 | 0.055 |  |  | 0.058
17 | 0.046 | 0.049 | 0.042 |  |  |  | 0.049
18 | 0.041 | 0.045 | 0.044 | 0.04 |  |  | 0.045
19 |  | 0.04 | 0.046 | 0.041 | 0.048 |  | 0.048
20 | 0.036 | 0.039 | 0.034 |  |  |  | 0.039
21 | 0.033 | 0.036 | 0.037 | 0.035 |  |  | 0.037
22 | 0.031 | 0.034 | 0.03 | 0.031 |  |  | 0.034
23 | 0.039 | 0.043 | 0.038 |  |  |  | 0.043
24 | 0.05 | 0.051 | 0.055 | 0.053 |  |  | 0.055
25 |  | 0.054 | 0.056 | 0.058 |  |  | 0.058
26 | 0.053 | 0.058 | 0.057 | 0.059 |  |  | 0.059
27 | 0.051 | 0.05 | 0.054 | 0.055 | 0.05 |  | 0.055
28 | 0.052 | 0.055 | 0.058 | 0.06 |  |  | 0.06
29 | 0.054 | 0.053 |  |  |  |  | 0.054
30 | 0.047 | 0.049 | 0.045 |  |  | 0.044 | 0.049
31 | 0.04 | 0.047 | 0.041 | 0.044 |  |  | 0.047
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 04/09/23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2023-03-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.85 | 58 | 49.3 | 12.5 | 7 | 31.6426 | YES | 5.55
2 | 0.88 | 58 | 51.04 | 12.7 | 7.01 | 31.4465 | YES | 4.72
3 | 0.87 | 58 | 50.46 | 13.1 | 6.99 | 30.3577 | YES | 6.87
4 | 0.91 | 58 | 52.78 | 12.2 | 7.01 | 33.2804 | YES | 5.41
5 | 0.89 | 58 | 51.62 | 12.1 | 7.04 | 33.7627 | YES | 6.45
6 | 0.86 | 58 | 49.88 | 12.4 | 7.01 | 32.6811 | YES | 1.8
7 | 1.03 | 58 | 59.74 | 12.6 | 6.99 | 31.9646 | YES | 9.51
8 | 1.01 | 58 | 58.58 | 12.1 | 6.96 | 33.2906 | YES | 3.26
9 | 1 | 58 | 58 | 12 | 6.95 | 33.3534 | YES | 7.22
10 | 1.03 | 58 | 59.74 | 12.3 | 6.97 | 33.053 | YES | 3.54
11 | 1.02 | 58 | 59.16 | 13.5 | 6.99 | 30.0676 | YES | 5.97
12 | 1 | 58 | 58 | 12 | 7.01 | 34.0409 | YES | 5
13 | 0.86 | 58 | 49.88 | 12.5 | 7 | 31.6787 | YES | 4.51
14 | 0.77 | 58 | 44.66 | 12.6 | 6.99 | 31.032 | YES | 2.63
15 | 0.7 | 58 | 40.6 | 12.7 | 7.01 | 30.8083 | YES | 7.98
16 | 0.76 | 58 | 44.08 | 13 | 7 | 30.2923 | YES | 5.83
17 | 0.78 | 58 | 45.24 | 13.1 | 6.97 | 29.8258 | YES | 4.65
18 | 0.9 | 58 | 52.2 | 12.8 | 6.98 | 30.9627 | YES | 5.55
19 | 0.92 | 58 | 53.36 | 12.5 | 6.91 | 30.8501 | YES | 6.11
20 | 0.96 | 58 | 55.68 | 12.1 | 6.93 | 32.7746 | YES | 6.87
21 | 0.9 | 58 | 52.2 | 12.3 | 6.96 | 32.4785 | YES | 4.86
22 | 0.98 | 58 | 56.84 | 11.9 | 6.9 | 32.93 | YES | 4.37
23 | 1 | 58 | 58 | 11.6 | 6.97 | 34.4502 | YES | 5.27
24 | 1.01 | 58 | 58.58 | 11.8 | 6.93 | 33.5893 | YES | 9.58
25 | 1.03 | 58 | 59.74 | 11.6 | 6.96 | 34.446 | YES | 5.69
26 | 1.01 | 58 | 58.58 | 11.4 | 7 | 35.2932 | YES | 7.01
27 | 1.06 | 58 | 61.48 | 11.2 | 7.04 | 36.4448 | YES | 12.6
28 | 1.02 | 58 | 59.16 | 11.5 | 7.06 | 35.8348 | YES | 4.65
29 | 1.01 | 58 | 58.58 | 11 | 7.07 | 37.096 | YES | 4.37
30 | 1 | 58 | 58 | 11.6 | 7.03 | 35.1637 | YES | 5.27
31 | 1.06 | 58 | 61.48 | 12.6 | 6.97 | 31.8373 | YES | 4.79
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2