## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-04-01
System Name: | Rainbow Rock Village MHP.044 |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.044 | 0.041 |  |  | 0.039 | 0.044
2 | 0.041 | 0.045 | 0.046 | 0.042 |  |  | 0.046
3 |  | 0.035 | 0.038 | 0.036 |  |  | 0.038
4 | 0.044 | 0.041 | 0.047 |  | 0.042 |  | 0.047
5 | 0.035 | 0.037 | 0.034 |  |  | 0.031 | 0.037
6 | 0.03 | 0.033 | 0.031 |  |  |  | 0.033
7 |  | 0.03 | 0.033 | 0.035 |  |  | 0.035
8 |  | 0.028 | 0.026 |  |  |  | 0.028
9 |  | 0.035 | 0.038 | 0.037 | 0.041 |  | 0.041
10 |  | 0.031 | 0.033 |  |  |  | 0.033
11 | 0.05 | 0.05 | 0.053 | 0.054 |  |  | 0.054
12 | 0.046 | 0.048 |  |  |  | 0.049 | 0.048
13 | 0.05 | 0.052 | 0.055 |  |  |  | 0.055
14 | 0.049 | 0.05 | 0.047 |  |  |  | 0.05
15 | 0.05 | 0.055 |  |  |  |  | 0.055
16 | 0.052 | 0.058 | 0.05 | 0.055 |  |  | 0.058
17 | 0.046 | 0.049 | 0.042 |  |  |  | 0.049
18 | 0.041 | 0.045 | 0.044 | 0.04 |  |  | 0.045
19 |  | 0.04 | 0.046 | 0.041 | 0.048 |  | 0.048
20 | 0.036 | 0.039 | 0.034 |  |  |  | 0.039
21 | 0.033 | 0.036 | 0.037 | 0.035 |  |  | 0.037
22 | 0.031 | 0.034 | 0.03 | 0.031 |  |  | 0.034
23 | 0.039 | 0.043 | 0.038 |  |  |  | 0.043
24 | 0.05 | 0.051 | 0.055 | 0.053 |  |  | 0.055
25 |  | 0.054 | 0.056 | 0.058 |  |  | 0.058
26 | 0.053 | 0.058 | 0.057 | 0.059 |  |  | 0.059
27 | 0.051 | 0.05 | 0.054 | 0.055 | 0.056 |  | 0.055
28 | 0.052 | 0.055 | 0.058 | 0.06 |  |  | 0.06
29 | 0.054 | 0.053 |  |  |  | 0.05 | 0.054
30 | 0.047 | 0.049 | 0.045 |  |  | 0.044 | 0.049
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 05-09-23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2023-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.89 | 58 | 51.62 | 12.1 | 7 | 33.3068 | YES | 1.16
2 | 0.91 | 58 | 52.78 | 12.2 | 6.97 | 32.832 | YES | 4.79
3 | 0.94 | 58 | 54.52 | 12.5 | 6.95 | 31.382 | YES | 4.23
4 | 0.96 | 58 | 55.68 | 12.4 | 6.92 | 32.048 | YES | 6.38
5 | 0.97 | 58 | 56.26 | 12.6 | 6.9 | 30.706 | YES | 1.73
6 | 1.02 | 58 | 59.16 | 12.3 | 6.93 | 32.5727 | YES | 7.98
7 | 1 | 58 | 58 | 11.9 | 6.97 | 33.7958 | YES | 4.79
8 | 1.03 | 58 | 59.74 | 11.7 | 7 | 34.6965 | YES | 2.84
9 | 0.98 | 58 | 56.84 | 11.5 | 6.95 | 34.3603 | YES | 8.26
10 | 0.96 | 58 | 55.68 | 11 | 6.91 | 34.9209 | YES | 5.83
11 | 0.94 | 58 | 54.52 | 11.2 | 6.94 | 34.7548 | YES | 7.32
12 | 0.97 | 58 | 56.26 | 11.4 | 7.01 | 35.2588 | YES | 4.79
13 | 0.96 | 58 | 55.68 | 11.6 | 7.04 | 35.1294 | YES | 4.72
14 | 0.8 | 58 | 46.4 | 11.7 | 7.02 | 34.0645 | YES | 5.55
15 | 0.83 | 58 | 48.14 | 11.5 | 6.96 | 33.916 | YES | 5.2
16 | 0.82 | 58 | 47.56 | 10.9 | 6.94 | 34.9661 | YES | 5.06
17 | 0.88 | 58 | 51.04 | 10.7 | 6.91 | 35.2882 | YES | 5.13
18 | 0.79 | 58 | 45.82 | 10.6 | 6.98 | 36.0196 | YES | 5.06
19 | 0.77 | 58 | 44.66 | 12.5 | 6.95 | 30.7802 | YES | 6.25
20 | 0.78 | 58 | 45.24 | 12.7 | 6.93 | 30.1821 | YES | 5.83
21 | 0.8 | 58 | 46.4 | 12.6 | 6.98 | 31.0231 | YES | 4.51
22 | 0.82 | 58 | 47.56 | 13.2 | 6.9 | 28.9997 | YES | 6.45
23 | 0.86 | 58 | 49.88 | 13.6 | 6.93 | 28.6815 | YES | 5.34
24 | 0.89 | 58 | 51.62 | 13.8 | 6.9 | 28.0829 | YES | 4.02
25 | 0.92 | 58 | 53.36 | 13.4 | 6.92 | 29.1587 | YES | 4.93
26 | 0.94 | 58 | 54.52 | 13.6 | 6.93 | 28.9446 | YES | 5.69
27 | 0.96 | 58 | 55.68 | 13.1 | 7.02 | 31.0136 | YES | 5.55
28 | 0.98 | 58 | 56.84 | 12.8 | 7 | 31.4785 | YES | 4.37
29 | 0.94 | 58 | 54.52 | 12.3 | 7.01 | 33.1775 | YES | 8.82
30 | 0.91 | 58 | 52.78 | 12 | 7.01 | 33.7075 | YES | 4.51
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2