## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-05-01
System Name: | Rainbow Rock Village MHP.044 |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.044 | 0.041 |  |  |  | 0.044
2 | 0.041 | 0.045 | 0.046 | 0.042 |  |  | 0.046
3 |  | 0.035 | 0.038 | 0.036 |  |  | 0.038
4 | 0.044 | 0.041 | 0.047 |  | 0.042 |  | 0.047
5 | 0.035 | 0.037 | 0.034 |  |  | 0.031 | 0.037
6 | 0.03 | 0.033 | 0.031 |  |  |  | 0.033
7 |  | 0.03 | 0.033 | 0.035 |  |  | 0.035
8 |  | 0.028 | 0.026 |  |  |  | 0.028
9 |  | 0.035 | 0.038 | 0.037 | 0.041 |  | 0.041
10 |  | 0.031 | 0.033 |  |  |  | 0.033
11 | 0.05 | 0.05 | 0.053 | 0.054 |  |  | 0.054
12 | 0.046 | 0.048 |  |  |  |  | 0.048
13 | 0.05 | 0.052 | 0.055 |  |  |  | 0.055
14 | 0.049 | 0.05 | 0.047 |  |  |  | 0.05
15 | 0.05 | 0.055 |  |  |  |  | 0.055
16 | 0.052 | 0.058 | 0.05 | 0.055 |  |  | 0.058
17 | 0.046 | 0.049 | 0.042 |  |  |  | 0.049
18 | 0.041 | 0.045 | 0.044 | 0.04 |  |  | 0.045
19 |  | 0.04 | 0.046 | 0.041 | 0.048 |  | 0.048
20 | 0.036 | 0.039 | 0.034 |  |  |  | 0.039
21 | 0.033 | 0.036 | 0.037 | 0.035 |  |  | 0.037
22 | 0.031 | 0.034 | 0.03 | 0.031 |  |  | 0.034
23 | 0.039 | 0.043 | 0.038 |  |  |  | 0.043
24 | 0.05 | 0.051 | 0.055 | 0.053 |  |  | 0.055
25 |  | 0.054 | 0.56 | 0.058 |  |  | 0.058
26 | 0.053 | 0.058 | 0.057 | 0.059 |  |  | 0.059
27 | 0.051 | 0.05 | 0.054 | 0.055 | 0.056 |  | 0.055
28 | 0.052 | 0.055 | 0.058 | 0.06 |  |  | 0.06
29 | 0.054 | 0.053 |  |  |  |  | 0.054
30 | 0.047 | 0.049 | 0.045 |  |  | 0.044 | 0.049
31 | 0.066 | 0.069 | 0.054 |  |  | 0.058 | 0.069
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 06-09-23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2023-05-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 58 | 52.2 | 16.9 | 6.98 | 23.5282 | YES | 3.95
2 | 0.92 | 58 | 53.36 | 16.7 | 6.91 | 23.2848 | YES | 5.06
3 | 0.94 | 58 | 54.52 | 16.2 | 6.93 | 24.3171 | YES | 4.79
4 | 0.96 | 58 | 55.68 | 16.3 | 6.9 | 23.9401 | YES | 6.8
5 | 0.99 | 58 | 57.42 | 16.7 | 6.88 | 23.2111 | YES | 3.33
6 | 0.89 | 58 | 51.62 | 16.5 | 6.86 | 23.0836 | YES | 5.97
7 | 0.86 | 58 | 49.88 | 15.8 | 7.01 | 25.5002 | YES | 4.93
8 | 0.88 | 58 | 51.04 | 15.7 | 7.03 | 25.923 | YES | 10.9
9 | 0.9 | 58 | 52.2 | 15.4 | 7 | 26.2158 | YES | 5.69
10 | 0.92 | 58 | 53.36 | 15.7 | 7.02 | 25.9452 | YES | 6.45
11 | 0.94 | 58 | 54.52 | 15.6 | 7 | 25.9854 | YES | 3.95
12 | 0.96 | 58 | 55.68 | 15.2 | 6.99 | 26.6532 | YES | 5.83
13 | 0.97 | 58 | 56.26 | 15 | 6.97 | 26.8431 | YES | 9.02
14 | 0.99 | 58 | 57.42 | 16.2 | 6.95 | 24.6401 | YES | 5.34
15 | 0.97 | 58 | 56.26 | 16 | 6.91 | 24.5471 | YES | 4.86
16 | 0.89 | 58 | 51.62 | 16.8 | 6.93 | 23.2219 | YES | 4.51
17 | 0.91 | 58 | 52.78 | 16.6 | 6.97 | 23.9456 | YES | 5.41
18 | 0.93 | 58 | 53.94 | 17 | 6.95 | 23.1898 | YES | 5.41
19 | 0.96 | 58 | 55.68 | 17.2 | 6.9 | 22.5334 | YES | 7.91
20 | 0.98 | 58 | 56.84 | 17.4 | 6.88 | 22.1169 | YES | 2.84
21 | 0.97 | 58 | 56.26 | 17.3 | 6.93 | 22.6608 | YES | 4.3
22 | 0.95 | 58 | 55.1 | 17.6 | 7 | 22.7443 | YES | 4.65
23 | 0.98 | 58 | 56.84 | 17.4 | 7.03 | 23.393 | YES | 5.34
24 | 0.96 | 58 | 55.68 | 17.7 | 7 | 22.6177 | YES | 5.06
25 | 0.92 | 58 | 53.36 | 17.9 | 7.03 | 22.4633 | YES | 4.44
26 | 0.91 | 58 | 52.78 | 17.8 | 7.01 | 22.4207 | YES | 5.13
27 | 0.94 | 58 | 54.52 | 17.5 | 7 | 22.8716 | YES | 5.48
28 | 0.98 | 58 | 56.84 | 17.4 | 7.02 | 23.3057 | YES | 4.58
29 | 0.96 | 58 | 55.68 | 17.7 | 7.04 | 22.9585 | YES | 4.3
30 | 0.95 | 58 | 55.1 | 17.9 | 7.01 | 22.3729 | YES | 1.04
31 | 0.98 | 58 | 56.84 | 17.6 | 7.02 | 22.9942 | YES | 3.12
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2