## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-06-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.037 | 0.039 | 0.036 |  | 0.039
2 | 0.04 | 0.041 | 0.04 |  |  |  | 0.041
3 |  | 0.033 | 0.035 | 0.037 |  |  | 0.037
4 | 0.032 | 0.03 | 0.033 | 0.034 |  |  | 0.034
5 | 0.029 | 0.03 | 0.031 | 0.03 |  |  | 0.031
6 | 0.027 | 0.025 | 0.025 | 0.029 |  |  | 0.029
7 | 0.031 | 0.033 | 0.03 |  |  |  | 0.033
8 |  | 0.026 | 0.025 | 0.028 |  |  | 0.028
9 | 0.033 | 0.031 | 0.03 | 0.027 |  |  | 0.033
10 | 0.04 | 0.043 | 0.044 |  |  |  | 0.044
11 | 0.041 | 0.04 | 0.047 | 0.042 | 0.04 | 0.046 | 0.047
12 | 0.043 | 0.047 | 0.042 |  |  |  | 0.047
13 | 0.049 | 0.037 | 0.039 |  |  | 0.045 | 0.049
14 | 0.05 | 0.055 | 0.05 |  |  |  | 0.055
15 |  |  | 0.043 | 0.051 | 0.053 |  | 0.053
16 |  |  | 0.038 | 0.04 | 0.042 |  | 0.042
17 | 0.025 | 0.026 | 0.026 | 0.027 |  |  | 0.027
18 | 0.027 | 0.025 | 0.028 |  |  |  | 0.028
19 | 0.048 | 0.05 | 0.051 | 0.05 |  |  | 0.051
20 | 0.038 | 0.037 | 0.04 | 0.041 | 0.043 | 0.04 | 0.043
21 | 0.037 | 0.038 | 0.043 | 0.042 |  |  | 0.043
22 | 0.035 | 0.036 | 0.038 |  |  |  | 0.038
23 | 0.04 | 0.044 | 0.041 |  |  |  | 0.044
24 | 0.036 | 0.029 | 0.033 |  | 0.032 | 0.031 | 0.033
25 | 0.027 | 0.025 | 0.04 | 0.046 | 0.042 |  | 0.046
26 | 0.025 | 0.027 | 0.049 | 0.05 | 0.052 | 0.055 | 0.055
27 | 0.046 | 0.051 | 0.056 | 0.05 |  |  | 0.056
28 | 0.048 | 0.047 | 0.049 |  |  |  | 0.049
29 | 0.05 | 0.053 | 0.05 | 0.05 |  |  | 0.053
30 | 0.04 | 0.051 | 0.047 |  |  |  | 0.051
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 07-09-23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.85 | 58 | 49.3 | 14 | 7 | 28.6273 | YES | 5
2 | 0.83 | 58 | 48.14 | 14.2 | 7.02 | 28.3927 | YES | 5.2
3 | 0.89 | 58 | 51.62 | 15 | 7.04 | 27.3002 | YES | 5.76
4 | 0.91 | 58 | 52.78 | 15.2 | 7 | 26.5999 | YES | 8.54
5 | 0.94 | 58 | 54.52 | 15.6 | 7.02 | 26.1796 | YES | 2.77
6 | 0.97 | 58 | 56.26 | 15.8 | 6.98 | 25.5365 | YES | 5.76
7 | 0.94 | 58 | 54.52 | 15.7 | 6.97 | 25.5249 | YES | 4.79
8 | 1.02 | 58 | 59.16 | 15.2 | 6.96 | 26.5389 | YES | 5.62
9 | 1.01 | 58 | 58.58 | 15.4 | 6.97 | 26.2531 | YES | 5.62
10 | 1 | 58 | 58 | 15.7 | 6.94 | 25.4153 | YES | 5.34
11 | 1.03 | 58 | 59.74 | 14.6 | 6.93 | 27.3517 | YES | 7.5
12 | 0.98 | 58 | 56.84 | 14.5 | 6.97 | 27.7885 | YES | 6.18
13 | 0.99 | 58 | 57.42 | 14.2 | 6.99 | 28.5958 | YES | 6.11
14 | 0.97 | 58 | 56.26 | 14.6 | 6.94 | 27.2659 | YES | 6.2
15 | 0.94 | 58 | 54.52 | 14.8 | 6.9 | 26.415 | YES | 6.11
16 | 0.8 | 58 | 46.4 | 14.5 | 6.93 | 26.8207 | YES | 8.05
17 | 0.82 | 58 | 47.56 | 14.6 | 6.94 | 26.8022 | YES | 5.76
18 | 0.8 | 58 | 46.4 | 14.6 | 6.97 | 27.041 | YES | 6.25
19 | 0.84 | 58 | 48.72 | 14.8 | 6.95 | 26.6049 | YES | 4.3
20 | 0.88 | 58 | 51.04 | 14.4 | 6.96 | 27.5546 | YES | 5.83
21 | 0.86 | 58 | 49.88 | 14.7 | 6.98 | 27.1462 | YES | 6.18
22 | 0.89 | 58 | 51.62 | 14.9 | 7 | 27.0778 | YES | 5.34
23 | 0.85 | 58 | 49.3 | 15 | 7 | 26.7743 | YES | 5.76
24 | 0.84 | 58 | 48.72 | 15.2 | 7.02 | 26.5849 | YES | 4.93
25 | 0.88 | 58 | 51.04 | 15.4 | 7.04 | 26.5482 | YES | 6.66
26 | 0.9 | 58 | 52.2 | 15.6 | 7 | 25.8667 | YES | 6.45
27 | 0.94 | 58 | 54.52 | 15.8 | 7.03 | 25.9273 | YES | 6.73
28 | 0.96 | 58 | 55.68 | 15.7 | 7.04 | 26.2591 | YES | 7.63
29 | 0.99 | 58 | 57.42 | 15.5 | 7.02 | 26.5069 | YES | 6.11
30 | 1.02 | 58 | 59.16 | 15.2 | 7 | 26.9367 | YES | 6.38
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2