## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-08-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.035 | 0.038 | 0.036 |  |  | 0.038
2 |  | 0.031 | 0.03 | 0.04 | 0.043 |  | 0.043
3 |  | 0.04 | 0.047 | 0.05 | 0.051 | 0.054 | 0.054
4 |  | 0.05 | 0.054 | 0.056 |  |  | 0.056
5 |  | 0.035 | 0.038 | 0.05 |  |  | 0.05
6 | 0.033 | 0.033 |  |  |  |  | 0.033
7 | 0.039 | 0.04 | 0.046 | 0.048 | 0.045 | 0.045 | 0.048
8 |  | 0.029 | 0.026 |  |  |  | 0.029
9 | 0.027 | 0.025 | 0.026 | 0.03 |  |  | 0.03
10 |  | 0.03 | 0.037 | 0.039 |  |  | 0.039
11 | 0.025 | 0.027 | 0.039 | 0.044 | 0.047 | 0.058 | 0.058
12 |  | 0.025 |  |  | 0.038 | 0.036 | 0.038
13 |  | 0.03 | 0.027 | 0.025 |  |  | 0.03
14 | 0.04 | 0.041 | 0.066 | 0.06 | 0.063 | 0.063 | 0.066
15 | 0.05 | 0.045 |  |  |  |  | 0.05
16 |  | 0.049 | 0.053 | 0.036 | 0.039 | 0.035 | 0.053
17 |  | 0.045 |  |  |  |  | 0.045
18 | 0.047 | 0.048 | 0.045 | 0.067 | 0.069 | 0.065 | 0.069
19 | 0.06 | 0.051 | 0.055 | 0.063 | 0.061 | 0.06 | 0.063
20 | 0.041 | 0.045 |  |  |  |  | 0.045
21 | 0.05 | 0.051 | 0.054 |  |  |  | 0.054
22 | 0.051 | 0.057 | 0.053 |  |  |  | 0.057
23 | 0.06 | 0.061 | 0.063 | 0.062 |  |  | 0.063
24 | 0.049 | 0.044 |  |  |  |  | 0.049
25 | 0.045 | 0.035 | 0.038 |  |  |  | 0.045
26 | 0.036 | 0.038 | 0.04 |  |  |  | 0.04
27 | 0.044 | 0.043 | 0.044 |  |  |  | 0.044
28 | 0.04 | 0.056 | 0.054 | 0.057 |  |  | 0.057
29 |  | 0.031 | 0.028 | 0.027 | 0.025 |  | 0.031
30 | 0.03 | 0.029 | 0.027 | 0.038 |  |  | 0.038
31 | 0.028 | 0.026 |  |  |  |  | 0.028
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 09/09/23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2023-08-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.88 | 58 | 51.04 | 13.1 | 6.9 | 29.3947 | YES | 5.69
2 | 0.89 | 58 | 51.62 | 13.5 | 6.96 | 29.2973 | YES | 5.2
3 | 0.9 | 58 | 52.2 | 13 | 6.91 | 29.7695 | YES | 5.34
4 | 0.93 | 58 | 53.94 | 13.3 | 6.89 | 29.0624 | YES | 6.66
5 | 0.96 | 58 | 55.68 | 14 | 6.93 | 28.2452 | YES | 3.61
6 | 0.93 | 58 | 53.94 | 14.2 | 6.95 | 27.9817 | YES | 3.61
7 | 0.97 | 58 | 56.26 | 14.1 | 6.97 | 28.5094 | YES | 6.45
8 | 0.94 | 58 | 54.52 | 14.3 | 6.88 | 27.1121 | YES | 6.59
9 | 0.96 | 58 | 55.68 | 14.6 | 6.9 | 26.8326 | YES | 10.97
10 | 0.88 | 58 | 51.04 | 14.8 | 6.94 | 26.6276 | YES | 5.13
11 | 0.86 | 58 | 49.88 | 14.7 | 6.97 | 27.0455 | YES | 5.34
12 | 0.84 | 58 | 48.72 | 15.1 | 7 | 26.5651 | YES | 5.48
13 | 0.9 | 58 | 52.2 | 15.3 | 7.02 | 26.5893 | YES | 5.69
14 | 0.96 | 58 | 55.68 | 15 | 7 | 27.1133 | YES | 6.59
15 | 1.02 | 58 | 59.16 | 15.2 | 6.99 | 26.8367 | YES | 6.38
16 | 1 | 58 | 58 | 15.6 | 6.97 | 25.8739 | YES | 5.2
17 | 1.01 | 58 | 58.58 | 15.5 | 6.96 | 25.9809 | YES | 7.15
18 | 0.99 | 58 | 57.42 | 15.2 | 6.98 | 26.6455 | YES | 4.62
19 | 0.96 | 58 | 55.68 | 15.8 | 6.99 | 25.6025 | YES | 4.44
20 | 0.94 | 58 | 54.52 | 15.6 | 7.02 | 26.1796 | YES | 5.48
21 | 0.97 | 58 | 56.26 | 15.4 | 7.01 | 26.5252 | YES | 4.02
22 | 0.99 | 58 | 57.42 | 15.6 | 7.03 | 26.428 | YES | 5.34
23 | 1 | 58 | 58 | 15.9 | 7 | 25.6435 | YES | 5.06
24 | 1.03 | 58 | 59.74 | 16.1 | 7.02 | 25.5787 | YES | 4.58
25 | 1.01 | 58 | 58.58 | 16.3 | 7 | 24.993 | YES | 5.76
26 | 1 | 58 | 58 | 16.4 | 6.97 | 24.5215 | YES | 4.93
27 | 1.03 | 58 | 59.74 | 16.6 | 6.95 | 24.0971 | YES | 5.69
28 | 0.96 | 58 | 55.68 | 16.8 | 6.98 | 23.8507 | YES | 4.37
29 | 0.97 | 58 | 56.26 | 16.9 | 6.94 | 23.3664 | YES | 5.2
30 | 0.91 | 58 | 52.78 | 16.6 | 6.91 | 23.415 | YES | 5.34
31 | 0.94 | 58 | 54.52 | 16.3 | 6.94 | 24.2445 | YES | 5.83
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2