## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-09-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.036 | 0.038 |  |  |  | 0.038
2 |  | 0.03 | 0.031 | 0.03 |  |  | 0.031
3 | 0.033 | 0.04 | 0.043 | 0.041 |  |  | 0.043
4 | 0.041 | 0.043 | 0.045 |  |  |  | 0.045
5 | 0.033 | 0.035 |  |  |  |  | 0.035
6 | 0.025 | 0.027 | 0.026 | 0.028 |  |  | 0.028
7 | 0.05 | 0.053 | 0.051 |  |  |  | 0.053
8 | 0.053 | 0.056 | 0.054 |  |  |  | 0.056
9 |  | 0.05 | 0.053 | 0.06 | 0.063 | 0.06 | 0.063
10 | 0.03 | 0.031 | 0.033 |  |  |  | 0.033
11 |  | 0.028 | 0.025 | 0.027 | 0.026 | 0.025 | 0.028
12 | 0.031 | 0.03 |  |  |  |  | 0.031
13 | 0.025 | 0.026 | 0.039 |  |  |  | 0.039
14 | 0.04 | 0.043 | 0.047 |  |  |  | 0.047
15 |  | 0.05 | 0.048 | 0.046 |  |  | 0.05
16 |  | 0.055 | 0.051 | 0.053 |  |  | 0.055
17 | 0.056 | 0.06 | 0.062 | 0.061 |  |  | 0.062
18 | 0.064 | 0.063 | 0.061 |  |  |  | 0.064
19 |  | 0.05 | 0.05 | 0.057 | 0.056 | 0.059 | 0.059
20 | 0.054 | 0.057 |  |  |  |  | 0.057
21 | 0.049 | 0.047 | 0.045 |  |  |  | 0.049
22 |  | 0.04 | 0.043 | 0.041 | 0.042 |  | 0 |  | 3
23 | 0.051 | 0.056 | 0.055 |  |  |  | 0.056
24 | 0.039 | 0.037 | 0.035 | 0.038 |  |  | 0.039
25 | 0.041 | 0.038 |  |  |  |  | 0.041
26 | 0.04 | 0.04 | 0.041 |  |  |  | 0.041
27 | 0.038 | 0.036 | 0.034 |  |  |  | 0.038
28 | 0.027 | 0.025 | 0.028 | 0.026 |  |  | 0.028
29 | 0.025 | 0.028 | 0.027 | 0.03 |  |  | 0.03
30 | 0.031 | 0.033 | 0.032 | 0.031 |  |  | 0.033
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 10/09/23
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.83 | 58 | 48.14 | 14.3 | 7.01 | 28.0988 | YES | 4.93
2 | 0.81 | 58 | 46.98 | 14 | 7.03 | 28.816 | YES | 5.62
3 | 0.88 | 58 | 51.04 | 14.1 | 7.01 | 28.6402 | YES | 4.58
4 | 0.86 | 58 | 49.88 | 15.9 | 7 | 25.2355 | YES | 4.65
5 | 0.88 | 58 | 51.04 | 15.6 | 7.03 | 26.0974 | YES | 6.25
6 | 0.9 | 58 | 52.2 | 15.5 | 6.97 | 25.7514 | YES | 3.95
7 | 0.93 | 58 | 53.94 | 15.7 | 6.95 | 25.3064 | YES | 5.83
8 | 0.94 | 58 | 54.52 | 15.3 | 6.91 | 25.6395 | YES | 6.04
9 | 1 | 58 | 58 | 14.9 | 6.94 | 26.8155 | YES | 7.43
10 | 1.03 | 58 | 59.74 | 14.6 | 6.9 | 27.0483 | YES | 5.55
11 | 1 | 58 | 58 | 14.7 | 6.93 | 27.0761 | YES | 5.9
12 | 0.97 | 58 | 56.26 | 14.3 | 6.91 | 27.5104 | YES | 7.63
13 | 0.95 | 58 | 55.1 | 14.6 | 6.67 | 24.6014 | YES | 8.88
14 | 0.98 | 58 | 56.84 | 14.5 | 6.65 | 24.6678 | YES | 2.43
15 | 0.95 | 58 | 55.1 | 14 | 6.63 | 25.2334 | YES | 6.38
16 | 0.97 | 58 | 56.26 | 14.3 | 6.6 | 24.5113 | YES | 4.93
17 | 0.93 | 58 | 53.94 | 14.6 | 6.73 | 25.1004 | YES | 5.41
18 | 0.9 | 58 | 52.2 | 14.5 | 6.7 | 24.9026 | YES | 5.13
19 | 0.91 | 58 | 52.78 | 14 | 6.73 | 26.0713 | YES | 5.9
20 | 0.98 | 58 | 56.84 | 15.3 | 6.71 | 23.9063 | YES | 6.38
21 | 0.96 | 58 | 55.68 | 15.4 | 6.7 | 23.6033 | YES | 7.36
22 | 0.97 | 58 | 56.26 | 15 | 6.73 | 24.5476 | YES | 4.44
23 | 0.9 | 58 | 52.2 | 15.3 | 6.71 | 23.6877 | YES | 4.79
24 | 0.88 | 58 | 51.04 | 15.6 | 6.73 | 23.3349 | YES | 7.29
25 | 0.83 | 58 | 48.14 | 15.8 | 7.01 | 25.4127 | YES | 4.58
26 | 0.8 | 58 | 46.4 | 15.6 | 7.03 | 25.8595 | YES | 7.36
27 | 0.84 | 58 | 48.72 | 15.8 | 7.01 | 25.4418 | YES | 5.06
28 | 0.86 | 58 | 49.88 | 15.6 | 7 | 25.7485 | YES | 5.83
29 | 0.83 | 58 | 48.14 | 15.8 | 7.03 | 25.6028 | YES | 4.58
30 | 0.8 | 58 | 46.4 | 15.5 | 7.01 | 25.8403 | YES | 5.83
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2