## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-11-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.04 | 0.052 | 0.041 |  |  | 0.052
2 |  |  | 0.035 | 0.039 | 0.037 | 0.034 | 0.039
3 | 0.033 | 0.037 | 0.04 | 0.042 | 0.04 |  | 0.042
4 |  |  | 0.042 | 0.044 |  |  | 0.044
5 | 0.04 | 0.042 | 0.04 |  |  | 0.04 | 0.042
6 | 0.049 | 0.048 | 0.046 |  |  |  | 0.049
7 | 0.056 | 0.051 | 0.053 | 0.05 |  |  | 0.056
8 | 0.036 | 0.039 | 0.04 | 0.042 |  |  | 0.042
9 |  |  | 0.043 |  | 0.04 |  | 0.043
10 |  | 0.041 | 0.045 | 0.047 | 0.044 |  | 0.047
11 |  |  | 0.046 | 0.044 |  |  | 0.046
12 | 0.05 | 0.053 | 0.056 | 0.052 |  |  | 0.056
13 | 0.053 | 0.05 | 0.051 | 0.052 | 0.051 |  | 0.053
14 |  |  | 0.058 | 0.054 | 0.053 |  | 0.058
15 | 0.056 | 0.055 | 0.06 |  |  |  | 0.06
16 | 0.062 | 0.059 | 0.061 |  |  |  | 0.062
17 | 0.046 | 0.049 | 0.046 | 0.042 |  |  | 0.049
18 | 0.04 | 0.045 | 0.043 | 0.041 | 0.046 |  | 0.046
19 |  | 0.04 | 0.049 | 0.044 | 0.05 | 0.054 | 0.054
20 | 0.035 | 0.032 | 0.037 | 0.033 |  |  | 0.037
21 | 0.032 | 0.033 | 0.035 | 0.037 | 0.04 |  | 0.04
22 | 0.034 | 0.031 | 0.034 | 0.039 | 0.036 |  | 0.039
23 |  |  | 0.036 |  |  |  | 0.036
24 | 0.03 | 0.033 | 0.038 |  |  |  | 0.038
25 | 0.049 | 0.044 | 0.043 | 0.045 |  |  | 0.049
26 | 0.04 | 0.043 | 0.045 | 0.04 | 0.048 |  | 0.045
27 | 0.033 | 0.031 | 0.033 |  |  |  | 0.033
28 | 0.041 | 0.043 | 0.038 | 0.04 |  |  | 0.043
29 |  |  | 0.033 | 0.035 | 0.038 | 0.033 | 0.038
30 | 0.049 | 0.047 | 0.044 |  |  |  | 0.049
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 12-08-23
[5 empty] | PHONE #: (541) 254-1909 |  |  | Cert # T-070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2023-11-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.89 | 58 | 51.62 | 15.1 | 7.04 | 27.118 | YES | 5.2
2 | 0.86 | 58 | 49.88 | 14.9 | 7.02 | 27.1865 | YES | 6.25
3 | 0.83 | 58 | 48.14 | 14.2 | 7.07 | 28.9247 | YES | 5.62
4 | 0.99 | 58 | 57.42 | 14.6 | 7 | 27.9446 | YES | 4.23
5 | 0.93 | 58 | 53.94 | 14.5 | 7.01 | 28.044 | YES | 4.93
6 | 0.95 | 58 | 55.1 | 14.8 | 6.98 | 27.244 | YES | 4.3
7 | 0.98 | 58 | 56.84 | 14.2 | 6.96 | 28.2467 | YES | 8.88
8 | 1.01 | 58 | 58.58 | 14.6 | 6.95 | 27.4929 | YES | 5.13
9 | 1.02 | 58 | 59.16 | 14 | 6.94 | 28.5452 | YES | 3.47
10 | 1 | 58 | 58 | 14.5 | 6.99 | 28.0598 | YES | 4.58
11 | 1.03 | 58 | 59.74 | 14.3 | 6.94 | 28.0102 | YES | 9.58
12 | 0.98 | 58 | 56.84 | 14.6 | 7.01 | 28.0166 | YES | 5.62
13 | 0.89 | 58 | 51.62 | 14.2 | 6.96 | 27.9578 | YES | 5
14 | 0.95 | 58 | 55.1 | 14.4 | 6.94 | 27.5703 | YES | 5.34
15 | 0.93 | 58 | 53.94 | 14.3 | 7 | 28.3162 | YES | 4.37
16 | 0.91 | 58 | 52.78 | 14.5 | 7.02 | 28.0841 | YES | 4.72
17 | 0.87 | 58 | 50.46 | 14.4 | 7.03 | 28.2484 | YES | 4.3
18 | 0.85 | 58 | 49.3 | 13.8 | 7.01 | 29.1204 | YES | 4.37
19 | 0.82 | 58 | 47.56 | 13.7 | 7.03 | 29.4331 | YES | 4.51
20 | 0.84 | 58 | 48.72 | 14.1 | 6.98 | 28.1938 | YES | 5.34
21 | 0.9 | 58 | 52.2 | 14.3 | 6.99 | 28.1147 | YES | 5.69
22 | 0.93 | 58 | 53.94 | 14.5 | 6.95 | 27.4256 | YES | 4.09
23 | 0.95 | 58 | 55.1 | 14.4 | 6.97 | 27.8793 | YES | 8.47
24 | 1.01 | 58 | 58.58 | 14.8 | 6.95 | 27.1272 | YES | 5.34
25 | 0.97 | 58 | 56.26 | 14.6 | 6.98 | 27.6743 | YES | 4.51
26 | 0.95 | 58 | 55.1 | 14.1 | 7.01 | 28.87 | YES | 7.43
27 | 0.95 | 58 | 55.1 | 13.8 | 7.01 | 29.4546 | YES | 4.79
28 | 0.91 | 58 | 52.78 | 13.5 | 7.03 | 30.1366 | YES | 5
29 | 0.9 | 58 | 52.2 | 13.2 | 7.04 | 30.8251 | YES | 6.25
30 | 0.83 | 58 | 48.14 | 13.6 | 7.02 | 29.5543 | YES | 5.69
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2