## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-12-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.043 | 0.048 | 0.045 | 0.044 |  |  | 0.048
2 |  | 0.051 | 0.055 | 0.053 | 0.055 |  | 0.055
3 | 0.033 | 0.04 | 0.043 | 0.041 |  |  | 0.043
4 | 0.041 | 0.043 | 0.045 |  |  | 0.049 | 0.048
5 | 0.043 | 0.035 | 0.051 | 0.054 |  |  | 0.054
6 | 0.025 | 0.027 | 0.026 | 0.028 |  |  | 0.028
7 | 0.05 | 0.053 | 0.051 | 0.056 | 0.051 |  | 0.056
8 | 0.053 | 0.056 | 0.054 | 0.042 |  |  | 0.056
9 |  | 0.05 | 0.053 | 0.06 | 0.063 |  | 0.063
10 | 0.04 | 0.045 | 0.044 |  |  |  | 0.045
11 |  | 0.044 | 0.046 | 0.038 | 0.044 |  | 0.046
12 | 0.041 | 0.044 | 0.046 | 0.05 |  |  | 0.05
13 | 0.035 | 0.036 | 0.049 | 0.04 |  |  | 0.049
14 | 0.038 | 0.045 | 0.041 | 0.036 |  |  | 0.045
15 |  | 0.05 | 0.048 | 0.046 |  |  | 0.05
16 |  | 0.055 | 0.051 | 0.053 |  |  | 0.055
17 | 0.056 | 0.06 | 0.062 |  |  |  | 0.062
18 | 0.064 | 0.063 | 0.061 | 0.056 |  |  | 0.064
19 |  | 0.05 | 0.05 | 0.057 | 0.056 |  | 0.057
20 | 0.054 | 0.057 | 0.053 |  |  |  | 0.057
21 | 0.049 | 0.047 | 0.045 | 0.049 |  |  | 0.049
22 |  | 0.04 | 0.043 | 0.041 | 0.042 |  | 0 |  | 3
23 |  | 0.056 | 0.055 | 0.052 |  |  | 0.056
24 | 0.039 | 0.037 | 0.035 | 0.038 |  |  | 0.039
25 | 0.041 | 0.038 | 0.039 | 0.033 |  |  | 0.041
26 | 0.04 | 0.04 | 0.041 | 0.035 |  |  | 0.041
27 | 0.038 | 0.036 | 0.034 | 0.036 |  |  | 0.038
28 |  | 0.025 | 0.028 | 0.026 | 0.041 |  | 0.041
29 | 0.025 | 0.028 | 0.027 | 0.03 |  |  | 0.03
30 |  | 0.033 | 0.032 | 0.031 | 0.036 |  | 0.036
31 |  |  | 0.044 | 0.046 | 0.038 | 0.033 | 0.046
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 01/09/24
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2023-12-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.93 | 58 | 53.94 | 14.1 | 6.99 | 28.5911 | YES | 4.11
2 | 0.91 | 58 | 52.78 | 14 | 7.03 | 29.1468 | YES | 5.02
3 | 0.89 | 58 | 51.62 | 13.8 | 7.02 | 29.3624 | YES | 4.69
4 | 0.99 | 58 | 57.42 | 13.7 | 7 | 29.6773 | YES | 5.06
5 | 1.04 | 58 | 60.32 | 14.2 | 7.06 | 29.5164 | YES | 5.25
6 | 1.02 | 58 | 59.16 | 14.5 | 6.97 | 27.9158 | YES | 4.65
7 | 0.93 | 58 | 53.94 | 13.7 | 6.97 | 29.1486 | YES | 5.98
8 | 0.96 | 58 | 55.68 | 14 | 6.91 | 28.0362 | YES | 6.04
9 | 1.03 | 58 | 59.74 | 13.9 | 6.94 | 28.7695 | YES | 6.59
10 | 1 | 58 | 58 | 14.2 | 6.89 | 27.5844 | YES | 5.55
11 | 1.02 | 58 | 59.16 | 14.3 | 7 | 28.6087 | YES | 6.63
12 | 0.96 | 58 | 55.68 | 14.7 | 6.98 | 27.4583 | YES | 5.68
13 | 0.94 | 58 | 54.52 | 14.1 | 6.72 | 25.8896 | YES | 6.88
14 | 0.88 | 58 | 51.04 | 14.2 | 6.78 | 26.1176 | YES | 5.67
15 | 0.85 | 58 | 49.3 | 14 | 6.89 | 27.481 | YES | 6.24
16 | 0.97 | 58 | 56.26 | 14.3 | 6.99 | 28.3404 | YES | 5.74
17 | 0.93 | 58 | 53.94 | 14.6 | 7.02 | 27.9607 | YES | 4.57
18 | 0.86 | 58 | 49.88 | 14.4 | 7.04 | 28.3212 | YES | 5.13
19 | 0.85 | 58 | 49.3 | 14.2 | 6.99 | 28.1422 | YES | 5.25
20 | 1.03 | 58 | 59.74 | 14.7 | 6.81 | 25.9827 | YES | 5.88
21 | 1 | 58 | 58 | 14.4 | 6.8 | 26.3214 | YES | 6.59
22 | 0.97 | 58 | 56.26 | 14 | 6.83 | 27.246 | YES | 5.44
23 | 1.01 | 58 | 58.58 | 14.3 | 6.82 | 26.7269 | YES | 5.64
24 | 0.99 | 58 | 57.42 | 14.6 | 6.87 | 26.626 | YES | 7.29
25 | 0.93 | 58 | 53.94 | 14.2 | 7.02 | 28.7187 | YES | 6.89
26 | 0.91 | 58 | 52.78 | 14.3 | 7.03 | 28.5681 | YES | 7.25
27 | 0.93 | 58 | 53.94 | 14.8 | 7 | 27.3846 | YES | 6.16
28 | 1.01 | 58 | 58.58 | 14.3 | 6.98 | 28.3646 | YES | 5.75
29 | 0.88 | 58 | 51.04 | 14.7 | 7.03 | 27.7188 | YES | 5.25
30 | 0.85 | 58 | 49.3 | 14.5 | 7.02 | 27.8923 | YES | 5.83
31 | 0.84 | 58 | 48.72 | 14.3 | 7 | 28.0266 | YES | 4.37
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2