## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-01-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.045 | 0.042 | 0.044 | 0.036 | 0.038 |  | 0.045
2 | 0.036 | 0.042 | 0.035 |  |  | 0.039 | 0.042
3 | 0.044 | 0.043 | 0.032 |  |  |  | 0.044
4 | 0.032 | 0.033 | 0.038 | 0.041 |  | 0.038 | 0.041
5 |  |  | 0.036 | 0.049 | 0.051 | 0.055 | 0.055
6 |  | 0.059 | 0.051 | 0.054 |  |  | 0.059
7 | 0.056 | 0.059 | 0.055 | 0.054 |  | 0.059 | 0.059
8 | 0.054 | 0.051 |  |  | 0.055 | 0.069 | 0.069
9 | 0.068 | 0.062 | 0.063 |  |  |  | 0.068
10 | 0.059 | 0.053 | 0.059 | 0.055 | 0.051 | 0.054 | 0.059
11 |  |  |  | 0.056 | 0.057 | 0.055 | 0.057
12 | 0.048 | 0.048 | 0.044 | 0.058 | 0.053 |  | 0.058
13 |  |  |  | 0.051 | 0.069 | 0.058 | 0.069
14 | 0.058 |  |  | 0.049 | 0.044 |  | 0.058
15 | 0.043 |  |  | 0.059 | 0.054 | 0.058 | 0.059
16 | 0.058 |  |  |  | 0.054 | 0.056 | 0.058
17 |  | 0.059 | 0.071 | 0.059 | 0.051 |  | 0.071
18 |  |  |  | 0.068 | 0.061 | 0.056 | 0.068
19 | 0.062 | 0.065 | 0.066 | 0.062 |  |  | 0.066
20 |  |  |  | 0.068 | 0.065 | 0.063 | 0.068
21 | 0.061 | 0.051 | 0.056 |  |  |  | 0.061
22 |  |  | 0.059 | 0.063 | 0.064 | 0.068 | 0.068
23 |  |  |  | 0.051 | 0.059 | 0.062 | 0.062
24 | 0.065 |  |  |  | 0.069 | 0.068 | 0.069
25 |  | 0.065 | 0.063 | 0.068 | 0.065 |  | 0.068
26 |  |  | 0.061 | 0.062 | 0.065 |  | 0.065
27 |  | 0.067 | 0.053 | 0.058 | 0.056 |  | 0.067
28 |  |  | 0.059 | 0.059 |  | 0.064 | 0.064
29 | 0.063 | 0.068 | 0.061 |  | 0.056 | 0.058 | 0.068
30 |  |  |  |  | 0.068 | 0.065 | 0.068
31 |  |  | 0.064 | 0.068 | 0.062 |  | 0.068
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | 2024-02-09
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2024-01-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.78 | 58 | 45.24 | 13.6 | 6.79 | 26.9798 | YES | 7.13
2 | 0.91 | 58 | 52.78 | 13.4 | 6.58 | 25.667 | YES | 8.79
3 | 0.86 | 58 | 49.88 | 12.6 | 6.62 | 27.3297 | YES | 8.65
4 | 0.88 | 58 | 51.04 | 12.7 | 6.78 | 28.8759 | YES | 8.17
5 | 0.91 | 58 | 52.78 | 13 | 6.55 | 26.0718 | YES | 8.21
6 | 0.94 | 58 | 54.52 | 13.5 | 6.47 | 24.5554 | YES | 8.44
7 | 0.99 | 58 | 57.42 | 13.4 | 6.59 | 25.9999 | YES | 8.93
8 | 1.03 | 58 | 59.74 | 13.7 | 6.57 | 25.409 | YES | 7.13
9 | 0.93 | 58 | 53.94 | 13.6 | 6.59 | 25.4778 | YES | 8.51
10 | 0.95 | 58 | 55.1 | 13.4 | 6.79 | 27.8799 | YES | 8.4
11 | 0.87 | 58 | 50.46 | 13.6 | 6.87 | 28.0815 | YES | 8.62
12 | 0.95 | 58 | 55.1 | 13.5 | 6.98 | 29.7181 | YES | 7.96
13 | 0.96 | 58 | 55.68 | 13.4 | 6.72 | 27.1949 | YES | 7.71
14 | 0.87 | 58 | 50.46 | 13 | 6.76 | 28.061 | YES | 8.33
15 | 0.98 | 58 | 56.84 | 13.4 | 6.88 | 28.9264 | YES | 5.66
16 | 1 | 58 | 58 | 12.9 | 6.79 | 28.9928 | YES | 8.28
17 | 1.04 | 58 | 60.32 | 13.5 | 6.56 | 25.6858 | YES | 6.17
18 | 0.99 | 58 | 57.42 | 13.6 | 6.58 | 25.5581 | YES | 8.98
19 | 0.97 | 58 | 56.26 | 12.9 | 6.62 | 27.1253 | YES | 6.78
20 | 0.86 | 58 | 49.88 | 13.4 | 6.84 | 28.1121 | YES | 8.4
21 | 0.86 | 58 | 49.88 | 13.1 | 6.51 | 25.3689 | YES | 8.79
22 | 0.98 | 58 | 56.84 | 13.3 | 6.56 | 25.8544 | YES | 9.12
23 | 0.99 | 58 | 57.42 | 13.4 | 6.34 | 23.6857 | YES | 8.68
24 | 0.97 | 58 | 56.26 | 13 | 6.47 | 25.481 | YES | 8.44
25 | 1.01 | 58 | 58.58 | 13.5 | 6.48 | 24.8458 | YES | 8.26
26 | 0.91 | 58 | 52.78 | 13.4 | 6.88 | 28.6962 | YES | 7.35
27 | 0.93 | 58 | 53.94 | 13.6 | 6.92 | 28.8045 | YES | 7.78
28 | 1.01 | 58 | 58.58 | 13.3 | 6.98 | 30.3244 | YES | 6.84
29 | 0.88 | 58 | 51.04 | 13.5 | 7.03 | 30.0337 | YES | 7.96
30 | 0.91 | 58 | 52.78 | 13.4 | 6.59 | 25.7628 | YES | 8.77
31 | 0.92 | 58 | 53.36 | 12.9 | 7 | 31.0563 | YES | 8.65
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2