## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-02-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.033 | 0.032 |  |  |  | 0.033
2 |  | 0.044 | 0.047 | 0.049 |  |  | 0.049
3 | 0.048 | 0.05 | 0.055 |  | 0.052 |  | 0.055
4 |  | 0.046 | 0.041 | 0.043 |  |  | 0.046
5 | 0.037 | 0.04 | 0.048 |  |  |  | 0.048
6 | 0.05 | 0.051 | 0.053 | 0.053 |  |  | 0.053
7 | 0.051 | 0.056 | 0.051 |  |  |  | 0.056
8 | 0.048 | 0.049 | 0.045 |  |  |  | 0.049
9 | 0.036 | 0.039 | 0.041 | 0.043 | 0.046 | 0.048 | 0.049
10 | 0.043 | 0.046 | 0.049 |  |  |  | 0.049
11 |  | 0.051 | 0.053 | 0.055 | 0.057 |  | 0.057
12 | 0.051 | 0.055 | 0.059 |  |  |  | 0.059
13 | 0.039 | 0.036 | 0.033 | 0.039 | 0.044 | 0.046 | 0.046
14 | 0.05 | 0.052 | 0.051 | 0.038 |  |  | 0.052
15 |  |  | 0.033 | 0.36 |  |  | 0.036
16 | 0.032 | 0.034 | 0.031 |  |  |  | 0.034
17 | 0.04 | 0.043 | 0.041 | 0.035 | 0.038 |  | 0.038
18 |  | 0.033 | 0.035 | 0.034 | 0.037 |  | 0.037
19 |  | 0.027 | 0.028 | 0.03 | 0.033 |  | 0.033
20 |  | 0.035 | 0.033 | 0.035 |  |  | 0.035
21 | 0.039 | 0.037 | 0.034 |  |  |  | 0.039
22 |  |  | 0.05 | 0.048 | 0.046 | 0.044 | 0.05
23 | 0.046 | 0.042 | 0 |  |  |  | 0.046
24 |  |  | 0.05 | 0.051 | 0.054 | 0.053 | 0.054
25 | 0.048 | 0.045 | 0.043 | 0.029 | 0.025 | 0.027 | 0.048
26 | 0.029 | 0.03 | 0.032 | 0.025 |  |  | 0.032
27 |  |  | 0.029 |  |  |  | 0.029
28 | 0.03 | 0.031 | 0.036 | 0.039 |  |  | 0.036
29 |  |  | 0.034 | 0.046 | 0.044 | 0.049 | 0.049
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | 2024-03-08
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2024-02-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.81 | 58 | 46.98 | 10.2 | 7 | 37.2994 | YES | 6.74
2 | 0.86 | 58 | 49.88 | 10 | 6.75 | 34.8676 | YES | 6.25
3 | 0.88 | 58 | 51.04 | 10.6 | 6.8 | 34.2056 | YES | 7.15
4 | 0.84 | 58 | 48.72 | 10.9 | 6.83 | 33.7527 | YES | 5.83
5 | 0.9 | 58 | 52.2 | 10.5 | 6.91 | 35.8238 | YES | 6.11
6 | 0.96 | 58 | 55.68 | 10.2 | 6.96 | 37.405 | YES | 7.56
7 | 0.95 | 58 | 55.1 | 10 | 6.93 | 37.4608 | YES | 6.45
8 | 0.98 | 58 | 56.84 | 10.5 | 6.9 | 36.0173 | YES | 6.45
9 | 0.93 | 58 | 53.94 | 10.9 | 7.02 | 36.3762 | YES | 6.31
10 | 0.9 | 58 | 52.2 | 10.3 | 7.03 | 37.8199 | YES | 6.94
11 | 0.95 | 58 | 55.1 | 10.1 | 7 | 38.1296 | YES | 7.63
12 | 0.97 | 58 | 56.26 | 10 | 6.93 | 37.544 | YES | 5.13
13 | 0.89 | 58 | 51.62 | 11.1 | 7 | 35.5082 | YES | 9.78
14 | 0.9 | 58 | 52.2 | 11.3 | 7.04 | 35.5774 | YES | 8.17
15 | 0.96 | 58 | 55.68 | 10.9 | 7 | 36.247 | YES | 6.66
16 | 0.91 | 58 | 52.78 | 10.3 | 6.6 | 32.6828 | YES | 6.87
17 | 1 | 58 | 58 | 12.7 | 6.66 | 27.9984 | YES | 7.84
18 | 1.01 | 58 | 58.58 | 12.4 | 6.68 | 29.728 | YES | 8.05
19 | 1.03 | 58 | 59.74 | 12.2 | 6.65 | 29.8668 | YES | 7.43
20 | 0.99 | 58 | 57.42 | 12.4 | 6.7 | 29.863 | YES | 6.31
21 | 0.9 | 58 | 52.2 | 12 | 6.77 | 31.0473 | YES | 7.5
22 | 1.01 | 58 | 58.58 | 12.1 | 6.79 | 31.4315 | YES | 7.01
23 | 0.88 | 58 | 51.04 | 12.2 | 6.75 | 30.3885 | YES | 7.43
24 | 0.86 | 58 | 49.88 | 12.3 | 6.8 | 30.642 | YES | 7.5
25 | 0.83 | 58 | 48.14 | 12.6 | 6.89 | 30.1081 | YES | 9.3
26 | 0.91 | 58 | 52.78 | 12.3 | 6.8 | 30.8076 | YES | 5.34
27 | 0.98 | 58 | 56.84 | 12.2 | 6.83 | 31.5544 | YES | 7.15
28 | 0.99 | 58 | 57.42 | 12.1 | 6.89 | 32.4396 | YES | 7.29
29 | 1.02 | 58 | 59.16 | 12 | 6.85 | 32.3126 | YES | 6.52
30
31 | [7 empty] | 8.65
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2