## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-03-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41-01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.042 | 0.041 | 0.044 |  |  |  | 0.044
2 |  |  | 0.037 | 0.036 | 0.038 | 0.04 | 0.04
3 | 0.042 | 0.04 | 0.043 |  |  |  | 0.043
4 | 0.05 | 0.05 | 0.052 | 0.048 | 0.045 | 0.043 | 0.052
5 | 0.047 | 0.045 | 0.047 | 0.041 |  |  | 0.047
6 |  |  | 0.041 | 0.04 | 0.042 |  | 0.042
7 |  |  | 0.04 | 0.035 | 0.038 | 0.035 | 0.04
8 | 0.033 |  | 0.038 |  |  |  | 0.038
9 |  | 0.036 | 0.041 | 0.05 | 0.055 | 0.057 | 0.057
10 | 0.053 |  | 0.053 | 0.053 |  |  | 0.053
11 |  | 0.05 | 0.048 | 0.043 | 0.052 | 0.05 | 0.052
12 | 0.054 |  | 0.05 |  |  |  | 0.054
13 |  | 0.052 | 0.044 | 0.047 | 0.045 | 0.043 | 0.047
14 | 0.035 |  | 0.036 |  |  |  | 0.036
15 | 0.044 | 0.033 | 0.04 | 0.036 | 0.035 | 0.033 | 0.047
16 | 0.028 | 0.047 | 0.036 | 0.029 | 0.027 | 0.025 | 0.036
17 |  |  | 0.031 |  |  |  | 0.031
18 |  | 0.029 | 0.035 | 0.037 | 0.035 | 0.033 | 0.037
19 | 0.034 |  | 0.036 |  |  |  | 0.039
20 | 0.033 | 0.039 | 0.031 | 0.032 |  |  | 0.035
21 | 0.03 | 0.035 | 0.03 |  |  |  | 0.031
22 | 0.03 | 0.035 | 0.029 |  |  |  | 0.035
23 |  | 0.029 | 0.029 | 0.03 | 0.033 | 0.034 | 0.033
24 |  |  | 0.03 |  |  |  | 0.03
25 | 0.031 | 0.038 | 0.036 |  |  |  | 0.038
26 |  | 0.029 | 0.03 | 0.031 | 0.033 | 0.03 | 0.033
27 | 0.029 | 0.027 | 0.029 |  |  |  | 0.029
28 |  | 0.041 | 0.038 | 0.041 |  |  | 0.041
29 |  |  | 0.029 | 0.025 | 0.027 | 0.029 | 0.029
30 | 0.028 | 0.029 | 0.028 | 0.026 |  |  | 0.028
31 |  |  | 0.033 | 0.035 | 0.038 | 0.044 | 0.044
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | 2024-03-01
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #: T070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41-01062 |  | Month/Year: | 2024-03-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 58 | 58 | 12.1 | 6.9 | 32.5849 | YES | 6.8
2 | 1.02 | 58 | 59.16 | 12 | 6.93 | 33.2001 | YES | 8.61
3 | 0.98 | 58 | 56.84 | 12.3 | 6.99 | 33.0971 | YES | 8.64
4 | 0.91 | 58 | 52.78 | 11.9 | 6.97 | 33.4651 | YES | 7.08
5 | 0.97 | 58 | 56.26 | 11.7 | 6.9 | 33.3156 | YES | 7.06
6 | 0.93 | 58 | 53.94 | 11.5 | 6.92 | 33.8253 | YES | 6.59
7 | 0.99 | 58 | 57.42 | 11.3 | 6.95 | 34.8416 | YES | 7.22
8 | 0.95 | 58 | 55.1 | 11.4 | 6.98 | 34.8223 | YES | 7.24
9 | 1 | 58 | 58 | 11.6 | 6.95 | 34.2161 | YES | 7.2
10 | 1.01 | 58 | 58.58 | 11.3 | 6.9 | 34.3272 | YES | 7.23
11 | 0.97 | 58 | 56.26 | 11.4 | 6.93 | 34.3083 | YES | 6.25
12 | 0.99 | 58 | 57.42 | 11.5 | 6.96 | 34.5156 | YES | 6.3
13 | 0.96 | 58 | 55.68 | 11.3 | 6.95 | 34.727 | YES | 7.29
14 | 0.94 | 58 | 54.52 | 11.1 | 6.91 | 34.6217 | YES | 6.59
15 | 0.9 | 58 | 52.2 | 11.3 | 6.93 | 34.2647 | YES | 8.12
16 | 0.99 | 58 | 57.42 | 11.6 | 6.91 | 33.7164 | YES | 6.94
17 | 0.87 | 58 | 50.46 | 11.5 | 6.99 | 34.4149 | YES | 6.81
18 | 0.9 | 58 | 52.2 | 11.7 | 6.97 | 33.8579 | YES | 6.88
19 | 0.95 | 58 | 55.1 | 11.4 | 6.99 | 34.9415 | YES | 6.8
20 | 0.98 | 58 | 56.84 | 11.3 | 6.93 | 34.5665 | YES | 6.73
21 | 1 | 58 | 58 | 11.6 | 6.94 | 34.0997 | YES | 6.73
22 | 1.03 | 58 | 59.74 | 11.8 | 6.97 | 34.1242 | YES | 7.56
23 | 1.04 | 58 | 60.32 | 11.5 | 6.99 | 35.063 | YES | 7.08
24 | 1.01 | 58 | 58.58 | 11.2 | 6.92 | 34.7844 | YES | 7.91
25 | 1.03 | 58 | 59.74 | 11 | 6.9 | 35.0704 | YES | 5.48
26 | 1 | 58 | 58 | 11.3 | 6.87 | 33.941 | YES | 2.34
27 | 1.01 | 58 | 58.58 | 11.2 | 6.81 | 33.5049 | YES | 6.94
28 | 1.03 | 58 | 59.74 | 10.8 | 6.88 | 35.2814 | YES | 0.9
29 | 0.99 | 58 | 57.42 | 10.9 | 6.87 | 34.7829 | YES | 4.79
30 | 0.9 | 58 | 52.2 | 11.7 | 6.8 | 31.9625 | YES | 8.33
31 | 1 | 58 | 58 | 11.9 | 6.83 | 32.2291 | YES | 6.8
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2