## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-04-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.041 | 0.047 | 0.046 | 0.044 | 0.045 | 0.047 | 0.046
2 | 0.047 | 0.045 | 0.048 | 0.031 | 0.033 | 0.03 | 0.07
3 | 0.03 | 0.035 | 0.039 | 0.033 | 0.031 | 0.038 | 0.038
4 | 0.034 | 0.037 | 0.036 | 0.032 | 0.039 | 0.035 | 0.037
5 | 0.04 | 0.043 | 0.044 | 0.049 | 0.047 | 0.043 | 0.049
6 | 0.05 | 0.051 | 0.049 | 0.03 | 0.033 | 0.034 | 0.051
7 | 0.052 | 0.049 | 0.045 | 0.033 | 0.035 | 0.038 | 0.052
8 | 0.041 | 0.042 | 0.04 | 0.033 | 0.03 | 0.028 | 0.042
9 | 0.027 | 0.029 | 0.033 | 0.029 | 0.027 | 0.029 | 0.033
10 | 0.031 | 0.036 | 0.039 | 0.05 | 0.053 | 0.058 | 0.058
11 | 0.048 | 0.044 | 0.046 | 0.041 | 0.044 | 0.048 | 0.048
12 | 0.043 | 0.042 | 0.04 | 0.035 | 0.033 | 0.03 | 0.042
13 | 0.031 | 0.03 | 0.029 | 0.033 | 0.038 | 0.035 | 0.038
14 | 0.043 | 0.04 | 0.044 |  |  |  | 0.044
15 |  |  | 0.028 | 0.03 | 0.033 | 0.031 | 0.033
16 | 0.031 | 0.03 | 0.033 |  |  |  | 0.033
17 |  |  | 0.028 | 0.033 | 0.035 | 0.036 | 0.036
18 | 0.035 | 0.033 | 0.03 | 0.029 | 0.027 | 0.026 | 0.035
19 | 0.028 | 0.03 | 0.032 | 0.33 | 0.038 | 0.036 | 0.038
20 | 0.04 | 0.044 | 0.045 | 0.038 | 0.041 | 0.046 | 0.046
21 | 0.034 | 0.038 | 0.032 | 0.036 | 0.038 | 0.037 | 0.038
22 | 0.049 | 0.045 | 0.044 | 0.042 | 0.04 | 0.041 | 0.049
23 | 0.029 | 0.031 | 0.033 | 0.03 | 0.038 | 0.03 | 0.038
24 | 0.033 | 0.034 | 0.036 | 0.029 | 0.026 | 0.028 | 0.036
25 | 0.026 | 0.029 | 0.025 | 0.033 | 0.038 | 0.035 | 0.033
26 | 0.032 | 0.04 | 0.041 | 0.044 | 0.038 | 0.036 | 0.044
27 | 0.04 | 0.043 | 0.045 |  |  | 0.055 | 0.055
28 | 0.062 | 0.052 | 0.056 | 0.054 | 0.057 |  | 0.062
29 |  | 0.052 | 0.059 | 0.054 | 0.056 | 0.058 | 0.059
30 | 0.054 | 0.055 | 0.059 | 0.051 | 0.055 | 0.052 | 0.059
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 05/01/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.88 | 58 | 51.04 | 11.9 | 7 | 33.6975 | YES | 5.34
2 | 0.86 | 58 | 49.88 | 11.8 | 7.03 | 34.1867 | YES | 6.87
3 | 0.8 | 58 | 46.4 | 11.5 | 7 | 34.2686 | YES | 6.45
4 | 0.88 | 58 | 51.04 | 11.3 | 7.01 | 35.1365 | YES | 6.45
5 | 0.9 | 58 | 52.2 | 11.1 | 7.03 | 35.9149 | YES | 5.83
6 | 0.96 | 58 | 55.68 | 11 | 7 | 36.0142 | YES | 6.59
7 | 0.9 | 58 | 52.2 | 11.2 | 7.02 | 35.5624 | YES | 6.66
8 | 0.93 | 58 | 53.94 | 11.4 | 7 | 34.9842 | YES | 5.34
9 | 0.91 | 58 | 52.78 | 11.6 | 6.98 | 34.2287 | YES | 6.25
10 | 0.89 | 58 | 51.62 | 11.8 | 6.9 | 32.8168 | YES | 5.9
11 | 0.85 | 58 | 49.3 | 11.9 | 6.93 | 32.7989 | YES | 6.52
12 | 0.8 | 58 | 46.4 | 11.7 | 6.9 | 32.7042 | YES | 6.04
13 | 0.79 | 58 | 45.82 | 11.5 | 6.94 | 33.5392 | YES | 3.51
14 | 0.83 | 58 | 48.14 | 11.8 | 6.99 | 33.614 | YES | 7.01
15 | 0.88 | 58 | 51.04 | 11.5 | 6.93 | 33.7556 | YES | 5.83
16 | 0.9 | 58 | 52.2 | 11.6 | 6.99 | 34.308 | YES | 7.22
17 | 0.97 | 58 | 56.26 | 11.8 | 7.02 | 34.4835 | YES | 6.25
18 | 0.99 | 58 | 57.42 | 11.9 | 7.04 | 34.5737 | YES | 6.87
19 | 1 | 58 | 58 | 11.6 | 7.03 | 35.1637 | YES | 6.45
20 | 1.03 | 58 | 59.74 | 11.4 | 7 | 35.3709 | YES | 7.08
21 | 1 | 58 | 58 | 12 | 7 | 33.9252 | YES | 6.31
22 | 1.02 | 58 | 59.16 | 12.1 | 7.04 | 34.2464 | YES | 6.8
23 | 1 | 58 | 58 | 11.8 | 7 | 34.3618 | YES | 6.66
24 | 0.96 | 58 | 55.68 | 11.7 | 7.01 | 34.5489 | YES | 6.52
25 | 0.91 | 58 | 52.78 | 11.8 | 7.03 | 34.3745 | YES | 6.87
26 | 0.89 | 58 | 51.62 | 11.9 | 7.01 | 33.8493 | YES | 6.18
27 | 0.87 | 58 | 50.46 | 11.8 | 7 | 33.8763 | YES | 8.4
28 | 0.98 | 58 | 56.84 | 12 | 6.94 | 33.1679 | YES | 6.46
29 | 1.06 | 58 | 61.48 | 12.3 | 6.92 | 32.6042 | YES | 5
30 | 0.99 | 58 | 57.42 | 11.9 | 7.05 | 34.692 | YES | 6.74
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2