## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-06-24
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.056 | 0.041 |  |  |  | 0.048 | 0.056
2 | 0.053 | 0.053 | 0.056 | 0.056 |  |  | 0.056
3 |  |  | 0.059 | 0.054 |  | 0.059 | 0.059
4 |  | 0.059 | 0.054 |  | 0.048 | 0.067 | 0.067
5 | 0.057 | 0.053 | 0.059 |  |  |  | 0.059
6 | 0.053 | 0.05 | 0.057 |  |  | 0.055 | 0.057
7 | 0.059 | 0.062 | 0.044 | 0.051 |  |  | 0.062
8 | 0.055 | 0.063 | 0.059 |  |  | 0.066 | 0.066
9 |  | 0.065 |  | 0.059 | 0.063 |  | 0.065
10 | 0.051 | 0.067 |  | 0.064 | 0.049 |  | 0.067
11 | 0.05 | 0.064 |  | 0.038 |  |  | 0.064
12 | 0.056 | 0.066 | 0.059 | 0.049 |  |  | 0.066
13 | 0.058 | 0.061 | 0.061 | 0.059 |  |  | 0.061
14 |  | 0.051 | 0.055 |  | 0.044 | 0.049 | 0.055
15 | 0.05 |  |  | 0.068 | 0.063 |  | 0.068
16 |  | 0.062 | 0.062 | 0.051 |  | 0.059 | 0.062
17 |  | 0.068 | 0.063 |  |  |  | 0.068
18 | 0.05 | 0.042 |  | 0.063 | 0.054 |  | 0.063
19 |  |  | 0.049 | 0.065 | 0.051 |  | 0.065
20 | 0.051 | 0.046 | 0.044 |  |  |  | 0.051
21 | 0.06 | 0.048 |  |  | 0.038 | 0.062 | 0.062
22 |  |  | 0.038 | 0.051 |  |  | 0.051
23 | 0.052 | 0.049 | 0.046 |  |  | 0.069 | 0.069
24 | 0.059 |  | 0.044 | 0.048 |  |  | 0.059
25 | 0.049 | 0.046 |  |  | 0.047 | 0.071 | 0.071
26 | 0.054 | 0.044 |  |  | 0.049 |  | 0.054
27 | 0.042 | 0.036 | 0.038 |  |  |  | 0.042
28 | 0.043 | 0.038 |  |  | 0.063 | 0.068 | 0.068
29 |  |  | 0.059 | 0.056 |  |  | 0.059
30 |  | 0.032 | 0.052 |  | 0.05 | 0.068 | 0.068
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: |  |  | DATE: 07/07/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-06-24 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.96 | 58 | 55.68 | 13.7 | 6.97 | 29.2485 | YES | 4.4
2 | 1.03 | 58 | 59.74 | 13.5 | 6.9 | 29.1135 | YES | 4.9
3 | 1.01 | 58 | 58.58 | 13.6 | 6.91 | 28.961 | YES | 4
4 | 1.06 | 58 | 61.48 | 13.7 | 6.8 | 27.7745 | YES | 3.9
5 | 0.99 | 58 | 57.42 | 14.7 | 6.86 | 26.35 | YES | 8.4
6 | 1.05 | 58 | 60.9 | 14.2 | 6.9 | 27.8458 | YES | 8.19
7 | 1.03 | 58 | 59.74 | 13.8 | 6.88 | 28.3244 | YES | 6.25
8 | 0.98 | 58 | 56.84 | 14 | 6.9 | 27.9961 | YES | 6.25
9 | 1 | 58 | 58 | 13.6 | 7.02 | 30.1328 | YES | 7.2
10 | 1.04 | 58 | 60.32 | 13.5 | 7 | 30.2482 | YES | 6.81
11 | 0.98 | 58 | 56.84 | 13.7 | 6.93 | 28.8834 | YES | 5.3
12 | 1.06 | 58 | 61.48 | 13.6 | 6.97 | 29.7823 | YES | 6.04
13 | 1.03 | 58 | 59.74 | 13.7 | 6.91 | 28.8338 | YES | 5.8
14 | 1.05 | 58 | 60.9 | 13.5 | 7.01 | 30.3952 | YES | 6.3
15 | 1.06 | 58 | 61.48 | 13.8 | 6.93 | 28.9541 | YES | 6.11
16 | 1.05 | 58 | 60.9 | 13.3 | 6.97 | 30.3502 | YES | 6.7
17 | 0.99 | 58 | 57.42 | 13.6 | 6.88 | 28.5749 | YES | 5.6
18 | 0.98 | 58 | 56.84 | 13.2 | 7.01 | 30.7634 | YES | 6.25
19 | 1.01 | 58 | 58.58 | 13.6 | 6.77 | 27.4934 | YES | 5.8
20 | 1.03 | 58 | 59.74 | 13.5 | 6.85 | 28.5781 | YES | 5.97
21 | 1.01 | 58 | 58.58 | 13.7 | 6.9 | 28.6614 | YES | 6.6
22 | 1 | 58 | 58 | 13.3 | 7 | 30.5152 | YES | 8.4
23 | 1.02 | 58 | 59.16 | 13.8 | 7.01 | 29.6907 | YES | 6
24 | 1.04 | 58 | 60.32 | 13.4 | 7.03 | 30.7912 | YES | 4.5
25 | 1.03 | 58 | 59.74 | 13.7 | 7 | 29.8129 | YES | 5.8
26 | 0.96 | 58 | 55.68 | 13.8 | 7.01 | 29.4882 | YES | 5.8
27 | 0.98 | 58 | 56.84 | 13.5 | 6.9 | 28.9479 | YES | 5.63
28 | 1.01 | 58 | 58.58 | 14.4 | 6.97 | 28.0711 | YES | 6.11
29 | 1.04 | 58 | 60.32 | 14.1 | 6.91 | 28.1049 | YES | 6
30 | 1.03 | 58 | 59.74 | 14.3 | 6.8 | 26.5895 | YES | 6.7
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2