## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-07-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.06 | 0.055 | 0.079 |  |  | 0.079
2 | 0.045 | 0.048 | 0.041 |  |  |  | 0.048
3 |  | 0.039 | 0.048 | 0.053 | 0.049 |  | 0.053
4 |  | 0.042 | 0.051 | 0.068 | 0.055 |  | 0.068
5 |  |  |  | 0.036 | 0.038 | 0.049 | 0.049
6 |  | 0.054 | 0.061 | 0.048 |  |  | 0.061
7 |  |  |  | 0.057 | 0.062 | 0.068 | 0.068
8 |  |  | 0.044 | 0.049 |  |  | 0.049
9 |  | 0.035 | 0.038 | 0.033 |  |  | 0.038
10 |  |  |  |  | 0.041 | 0.057 | 0.057
11 | 0.044 |  |  | 0.038 | 0.046 |  | 0.046
12 |  | 0.037 | 0.036 | 0.043 |  |  | 0.043
13 |  |  |  | 0.035 | 0.039 | 0.031 | 0.039
14 |  |  | 0.059 | 0.061 | 0.065 |  | 0.065
15 |  |  |  | 0.052 | 0.057 |  | 0.057
16 | 0.055 | 0.042 | 0.063 |  |  |  | 0.063
17 |  |  | 0.052 | 0.057 | 0.051 |  | 0.057
18 |  |  |  |  | 0.039 | 0.062 | 0.062
19 | 0.048 |  |  |  | 0.056 | 0.054 | 0.056
20 |  |  | 0.038 | 0.046 |  |  | 0.046
21 |  | 0.039 | 0.045 | 0.059 |  |  | 0.059
22 |  |  |  |  | 0.033 | 0.046 | 0.046
23 |  |  | 0.035 | 0.037 | 0.033 |  | 0.037
24 |  |  |  | .0.052 | 0.048 | 0.044 | 0.052
25 |  |  | 0.035 | 0.042 |  |  | 0.042
26 |  |  |  | 0.039 | 0.056 | 0.057 | 0.057
27 |  | 0.034 | 0.038 |  |  |  | 0.038
28 |  |  | 0.03 | 0.036 |  |  | 0.036
29 |  |  |  | 0.058 | 0.065 | 0.068 | 0.068
30 |  |  | 0.069 | 0.061 |  |  | 0.069
31 |  |  | 0.068 | 0.061 | 0.063 |  | 0.068
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 08/09/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-07-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.88 | 58 | 51.04 | 14.9 | 7.04 | 27.4521 | YES | 4.24
2 | 1.03 | 58 | 59.74 | 15.1 | 6.99 | 27.048 | YES | 6.88
3 | 1.06 | 58 | 61.48 | 14.7 | 6.87 | 26.6609 | YES | 6.25
4 | 0.94 | 58 | 54.52 | 15.3 | 7.01 | 26.612 | YES | 6.53
5 | 0.99 | 58 | 57.42 | 15.2 | 6.78 | 24.7326 | YES | 7.24
6 | 1 | 58 | 58 | 15.6 | 6.89 | 25.1141 | YES | 5.36
7 | 0.97 | 58 | 56.26 | 16 | 6.85 | 24.0036 | YES | 8.19
8 | 0.89 | 58 | 51.62 | 15.8 | 6.73 | 23.0495 | YES | 4.52
9 | 1.04 | 58 | 60.32 | 15.6 | 6.82 | 24.5796 | YES | 5.55
10 | 1.03 | 58 | 59.74 | 16.1 | 7.03 | 25.6742 | YES | 6.92
11 | 1.08 | 58 | 62.64 | 16.6 | 6.99 | 24.6001 | YES | 7.54
12 | 0.93 | 58 | 53.94 | 16.1 | 6.75 | 22.8631 | YES | 4.69
13 | 0.87 | 58 | 50.46 | 16.2 | 6.69 | 22.0528 | YES | 8.32
14 | 1.02 | 58 | 59.16 | 15.4 | 6.94 | 25.9913 | YES | 6.87
15 | 1.05 | 58 | 60.9 | 15.9 | 6.96 | 25.4093 | YES | 9.88
16 | 0.89 | 58 | 51.62 | 15.1 | 7.06 | 27.3204 | YES | 5.91
17 | 1.06 | 58 | 61.48 | 15.5 | 7.05 | 27.0198 | YES | 4.95
18 | 1.03 | 58 | 59.74 | 14.9 | 6.77 | 25.2574 | YES | 4.97
19 | 1.05 | 58 | 60.9 | 15.3 | 6.81 | 25.015 | YES | 5.34
20 | 1.05 | 58 | 60.9 | 15.6 | 6.76 | 24.063 | YES | 7.29
21 | 0.92 | 58 | 53.36 | 15.1 | 6.74 | 24.3344 | YES | 8.57
22 | 0.86 | 58 | 49.88 | 15 | 7.06 | 27.4098 | YES | 6.59
23 | 0.94 | 58 | 54.52 | 15.7 | 6.62 | 22.3984 | YES | 5.93
24 | 0.99 | 58 | 57.42 | 15.9 | 7 | 25.6141 | YES | 10.25
25 | 1 | 58 | 58 | 15.6 | 6.79 | 24.1947 | YES | 5.25
26 | 1.02 | 58 | 59.16 | 15.1 | 6.88 | 25.9335 | YES | 5.83
27 | 0.94 | 58 | 54.52 | 15.9 | 6.82 | 23.8142 | YES | 6.26
28 | 0.9 | 58 | 52.2 | 15.8 | 6.77 | 23.4235 | YES | 4.58
29 | 0.85 | 58 | 49.3 | 15.4 | 7.03 | 26.3589 | YES | 5.36
30 | 1.05 | 58 | 60.9 | 15.9 | 6.74 | 23.407 | YES | 6.38
31 | 1.02 | 58 | 59.16 | 15.2 | 6.81 | 25.097 | YES | 5.14
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2