## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-08-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.056 | 0.063 | 0.051 |  |  | 0.063
2 | 0.039 | 0.048 | 0.033 | 0.047 |  | 0.039 | 0.048
3 |  |  | 0.046 | 0.44 |  |  | 0.046
4 | 0.039 | 0.053 |  |  |  | 0.045 | 0.053
5 | 0.036 |  |  | 0.051 | 0.044 |  | 0.051
6 |  | 0.034 | 0.044 | 0.045 |  |  | 0.045
7 |  |  |  | 0.041 | 0.049 | 0.045 | 0.049
8 |  |  | 0.048 | 0.055 |  |  | 0.055
9 | 0.023 | 0.031 | 0.03 |  |  |  | 0.031
10 |  |  | 0.047 | 0.043 | 0.041 |  | 0.047
11 |  | 0.038 | 0.033 |  |  |  | 0.038
12 |  |  |  | 0.049 | 0.048 | 0.036 | 0.049
13 |  |  | 0.041 | 0.049 |  |  | 0.049
14 | 0.035 | 0.036 | 0.046 |  |  |  | 0.046
15 |  |  |  | 0.036 | 0.037 |  | 0.036
16 | 0.031 | 0.039 |  |  | 0.051 | 0.043 | 0.051
17 |  |  | 0.029 | 0.036 |  |  | 0.036
18 |  | 0.062 | 0.057 | 0.05 |  |  | 0.062
19 |  |  |  | 0.049 | 0.041 | 0.036 | 0.049
20 |  | 0.067 | 0.063 | 0.061 |  |  | 0.067
21 |  |  |  | 0.057 | 0.059 |  | 0.059
22 |  | 0.054 | 0.058 |  |  |  | 0.058
23 | 0.046 | 0.041 |  |  | 0.061 | 0.049 | 0.061
24 |  |  | 0.031 | 0.044 |  |  | 0.044
25 |  | 0.035 | 0.047 | 0.055 |  |  | 0.055
26 |  |  |  | 0.046 | 0.044 |  | 0.046
27 | 0.059 | 0.061 |  |  |  |  | 0.061
28 |  |  |  | 0.044 | 0.053 | 0.059 | 0.059
29 |  |  | 0.027 | 0.033 |  |  | 0.033
30 | 0.04 | 0.046 | 0.051 |  |  |  | 0.051
31 |  |  |  | 0.023 | 0.029 | 0.34 | 0.034
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 09/09/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 58 | 57.42 | 18.6 | 7.02 | 21.5205 | YES | 6.74
2 | 0.89 | 58 | 51.62 | 18.6 | 7.03 | 21.3538 | YES | 6.31
3 | 0.93 | 58 | 53.94 | 19.2 | 7 | 20.37 | YES | 4.25
4 | 0.88 | 58 | 51.04 | 18.6 | 6.96 | 20.7766 | YES | 5.59
5 | 0.84 | 58 | 48.72 | 18.3 | 6.92 | 20.79 | YES | 5.13
6 | 0.82 | 58 | 47.56 | 18.6 | 6.94 | 20.479 | YES | 6.14
7 | 0.85 | 58 | 49.3 | 18.2 | 6.95 | 21.1921 | YES | 6.64
8 | 0.94 | 58 | 54.52 | 18.4 | 7.02 | 21.6875 | YES | 4.89
9 | 0.92 | 58 | 53.36 | 18.8 | 6.94 | 20.4386 | YES | 5.16
10 | 0.83 | 58 | 48.14 | 18.5 | 6.95 | 20.7193 | YES | 6.11
11 | 0.87 | 58 | 50.46 | 18.9 | 6.97 | 20.4127 | YES | 5.83
12 | 0.83 | 58 | 48.14 | 19 | 7.03 | 20.6415 | YES | 6.52
13 | 0.84 | 58 | 48.72 | 19.2 | 6.91 | 19.4889 | YES | 7.29
14 | 0.82 | 58 | 47.56 | 19.4 | 6.97 | 19.6201 | YES | 7.15
15 | 0.96 | 58 | 55.68 | 19.1 | 6.89 | 19.7464 | YES | 5.34
16 | 0.92 | 58 | 53.36 | 18.5 | 6.92 | 20.7012 | YES | 7.5
17 | 1.01 | 58 | 58.58 | 18.9 | 7.01 | 21.0587 | YES | 7.01
18 | 1.06 | 58 | 61.48 | 19.2 | 6.82 | 19.3257 | YES | 6.25
19 | 0.86 | 58 | 49.88 | 19.1 | 6.85 | 19.2278 | YES | 6.26
20 | 0.88 | 58 | 51.04 | 19.3 | 6.86 | 19.0846 | YES | 6.77
21 | 0.89 | 58 | 51.62 | 19.2 | 6.99 | 20.2002 | YES | 6.17
22 | 0.93 | 58 | 53.94 | 19.1 | 7.02 | 20.6627 | YES | 5.13
23 | 0.99 | 58 | 57.42 | 18.9 | 6.84 | 19.711 | YES | 4.99
24 | 1.02 | 58 | 59.16 | 18.6 | 6.79 | 19.8094 | YES | 5.05
25 | 0.93 | 58 | 53.94 | 19.4 | 6.89 | 19.2822 | YES | 5.74
26 | 0.99 | 58 | 57.42 | 19.5 | 7 | 20.0997 | YES | 5.25
27 | 0.98 | 58 | 56.84 | 19.6 | 6.87 | 18.9895 | YES | 5.15
28 | 0.87 | 58 | 50.46 | 20 | 6.8 | 17.7713 | YES | 5.56
29 | 0.89 | 58 | 51.62 | 20.1 | 6.81 | 17.7589 | YES | 6.45
30 | 0.93 | 58 | 53.94 | 20 | 6.88 | 18.4438 | YES | 6.31
31 | 0.95 | 58 | 55.1 | 20.2 | 6.72 | 17.168 | YES | 5.94
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2