## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-09-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.05 | 0.059 | 0.064 |  | 0.064
2 |  | 0.039 | 0.048 |  |  | 0.055 | 0.055
3 | 0.051 | 0.068 |  |  | 0.042 | 0.049 | 0.068
4 |  |  | 0.058 | 0.064 | 0.063 |  | 0.064
5 |  | 0.057 | 0.055 | 0.056 |  |  | 0.057
6 | 0.049 | 0.044 |  |  | 0.051 | 0.055 | 0.055
7 |  |  | 0.071 | 0.079 | 0.067 |  | 0.079
8 | 0.043 | 0.049 |  |  |  | 0.072 | 0.072
9 | 0.081 | 0.073 |  | 0.061 | 0.065 |  | 0.081
10 |  | 0.051 | 0.059 | 0.063 |  |  | 0.063
11 |  |  |  | 0.055 | 0.05 |  | 0.055
12 | 0.075 | 0.071 | 0.075 |  |  |  | 0.075
13 |  | 0.031 | 0.039 | 0.049 |  |  | 0.049
14 |  | 0.033 | 0.036 | 0.041 |  |  | 0.041
15 |  |  |  | 0.046 | 0.054 | 0.055 | 0.055
16 |  |  | 0.055 | 0.058 |  |  | 0.058
17 | 0.063 | 0.06 |  |  | 0.053 | 0.055 | 0.063
18 |  |  | 0.074 | 0.071 |  |  | 0.074
19 | 0.063 | 0.065 |  |  | 0.042 | 0.044 | 0.65
20 |  |  | 0.063 | 0.067 | 0.059 |  | 0.067
21 |  | 0.047 | 0.044 | 0.042 |  |  | 0.047
22 | 0.033 | 0.026 | 0.049 |  |  |  | 0.049
23 |  | 0.057 | 0.051 | 0.055 |  |  | 0.057
24 | 0.039 | 0.046 | 0.055 |  | 0.046 | 0.053 | 0.055
25 |  |  | 0.057 | 0.063 |  |  | 0.063
26 | 0.044 | 0.046 | 0.044 |  |  |  | 0.046
27 |  | 0.062 | 0.06 | 0.068 |  |  | 0.068
28 | 0.049 | 0.053 |  |  | 0.052 | 0.056 | 0.056
29 |  |  | 0.051 | 0.043 |  |  | 0.051
30 | 0.039 | 0.031 | 0.033 |  |  | 0.044 | 0.044
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 10/07/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.98 | 58 | 56.84 | 12.5 | 6.87 | 30.6047 | YES | 4.55
2 | 0.94 | 58 | 54.52 | 12.8 | 6.73 | 28.3495 | YES | 5.01
3 | 1 | 58 | 58 | 12.4 | 6.84 | 31.331 | YES | 4.79
4 | 1.05 | 58 | 60.9 | 12.6 | 6.89 | 30.8726 | YES | 4.17
5 | 0.93 | 58 | 53.94 | 12.5 | 6.83 | 29.9828 | YES | 4.8
6 | 1.02 | 58 | 59.16 | 12.9 | 6.9 | 30.2693 | YES | 5.04
7 | 1.06 | 58 | 61.48 | 12.9 | 6.96 | 31.0913 | YES | 4.87
8 | 1.01 | 58 | 58.58 | 13.4 | 6.89 | 29.1336 | YES | 4.24
9 | 0.99 | 58 | 57.42 | 13.1 | 6.94 | 30.2106 | YES | 4.65
10 | 0.94 | 58 | 54.52 | 13.5 | 6.83 | 28.0766 | YES | 4.19
11 | 0.99 | 58 | 57.42 | 13.3 | 6.87 | 29.0457 | YES | 5.26
12 | 0.93 | 58 | 53.94 | 13.3 | 6.88 | 28.9547 | YES | 5.73
13 | 0.89 | 58 | 51.62 | 13.6 | 6.97 | 29.2103 | YES | 4.39
14 | 0.94 | 58 | 54.52 | 13.5 | 6.84 | 28.1811 | YES | 4.19
15 | 0.96 | 58 | 55.68 | 13.7 | 6.86 | 28.078 | YES | 5.19
16 | 1 | 58 | 58 | 13.9 | 6.81 | 27.3193 | YES | 5.55
17 | 0.88 | 58 | 51.04 | 13.6 | 6.99 | 29.3944 | YES | 5.32
18 | 0.96 | 58 | 55.68 | 14.1 | 6.86 | 27.3365 | YES | 4.7
19 | 1.02 | 58 | 59.16 | 14.4 | 6.85 | 26.8771 | YES | 4.19
20 | 0.89 | 58 | 51.62 | 13.9 | 6.8 | 26.8777 | YES | 5.24
21 | 1.03 | 58 | 59.74 | 14.3 | 6.88 | 27.3925 | YES | 4.56
22 | 0.99 | 58 | 57.42 | 14.4 | 6.83 | 26.5865 | YES | 4.72
23 | 1 | 58 | 58 | 14.5 | 6.81 | 26.2431 | YES | 5
24 | 0.87 | 58 | 50.46 | 14.1 | 6.89 | 27.3601 | YES | 5.48
25 | 0.91 | 58 | 52.78 | 14.6 | 6.85 | 26.1877 | YES | 4.98
26 | 1.05 | 58 | 60.9 | 14.3 | 6.85 | 27.1507 | YES | 4.42
27 | 0.97 | 58 | 56.26 | 14.5 | 6.8 | 26.056 | YES | 4.17
28 | 1.04 | 58 | 60.32 | 14.7 | 6.98 | 27.7105 | YES | 4.62
29 | 1.02 | 58 | 59.16 | 14.8 | 6.95 | 27.1583 | YES | 4.83
30 | 0.88 | 58 | 51.04 | 14.6 | 7.01 | 27.6983 | YES | 5.32
31 |  | 58
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2