## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-10-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.055 | 0.062 | 0.05 |  |  | 0.062
2 | 0.069 | 0.071 |  |  | 0.077 | 0.074 | 0.077
3 |  |  | 0.071 | 0.068 | 0.065 |  | 0.071
4 | 0.059 | 0.066 | 0.066 |  |  |  | 0.066
5 |  | 0.073 | 0.064 | 0.061 |  |  | 0.073
6 | 0.079 | 0.07 |  |  | 0.063 | 0.065 | 0.079
7 |  | 0.058 | 0.055 | 0.057 |  |  | 0.058
8 |  |  | 0.068 | 0.062 | 0.07 |  | 0.07
9 |  | 0.053 | 0.049 | 0.046 |  |  | 0.053
10 |  |  | 0.069 | 0.063 | 0.061 |  | 0.069
11 | 0.053 | 0.067 | 0.054 |  |  | 0.069 | 0.069
12 |  | 0.081 | 0.084 | 0.073 |  |  | 0.084
13 |  |  | 0.071 | 0.064 | 0.063 |  | 0.071
14 |  | 0.055 | 0.05 | 0.055 |  |  | 0.055
15 | 0.049 | 0.046 |  |  | 0.053 | 0.057 | 0.057
16 |  |  |  | 0.073 | 0.076 | 0.08 | 0.08
17 |  |  | 0.064 | 0.06 |  |  | 0.064
18 | 0.055 | 0.055 |  |  |  | 0.078 | 0.078
19 | 0.062 |  |  | 0.078 | 0.074 |  | 0.078
20 |  |  | 0.087 | 0.082 | 0.08 |  | 0.087
21 |  | 0.056 | 0.043 | 0.049 |  |  | 0.056
22 | 0.051 | 0.049 |  | 0.063 | 0.065 |  | 0.065
23 |  |  | 0.071 | 0.073 | 0.072 |  | 0.073
24 |  | 0.064 | 0.065 | 0.068 |  |  | 0.068
25 |  |  | 0.044 | 0.049 | 0.041 |  | 0.049
26 |  | 0.068 | 0.064 | 0.066 |  |  | 0.068
27 |  |  | 0.069 | 0.077 | 0.071 |  | 0.077
28 | 0.077 | 0.079 | 0.063 |  |  |  | 0.079
29 |  | 0.073 | 0.075 | 0.081 |  |  | 0.081
30 |  |  | 0.079 | 0.075 |  |  | 0.079
31 | 0.086 | 0.088 | 0.081 |  |  |  | 0.088
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 11/04/2024
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-10-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 58 | 58 | 12.3 | 7 | 33.2821 | YES | 6.45
2 | 1.03 | 58 | 59.74 | 12 | 7.03 | 34.3865 | YES | 4.44
3 | 1.01 | 58 | 58.58 | 12.3 | 7.06 | 34.0052 | YES | 4.79
4 | 0.93 | 58 | 53.94 | 13.6 | 7.01 | 29.7826 | YES | 4.16
5 | 0.99 | 58 | 57.42 | 14.2 | 6.96 | 28.279 | YES | 6.11
6 | 0.97 | 58 | 56.26 | 14.8 | 6.93 | 26.8033 | YES | 2.5
7 | 0.92 | 58 | 53.36 | 14.6 | 6.99 | 27.6191 | YES | 4.79
8 | 0.9 | 58 | 52.2 | 14.3 | 6.96 | 27.8031 | YES | 3.95
9 | 1.02 | 58 | 59.16 | 14.3 | 6.9 | 27.5654 | YES | 3.47
10 | 1.04 | 58 | 60.32 | 15.6 | 6.92 | 25.5131 | YES | 5.34
11 | 1.02 | 58 | 59.16 | 15.3 | 6.97 | 26.4599 | YES | 4.72
12 | 1 | 58 | 58 | 15 | 6.91 | 26.3407 | YES | 3.4
13 | 1.03 | 58 | 59.74 | 15.4 | 6.94 | 26.0211 | YES | 5.34
14 | 1.01 | 58 | 58.58 | 15.7 | 7.03 | 26.3117 | YES | 2.29
15 | 1.04 | 58 | 60.32 | 15.1 | 7 | 27.1798 | YES | 4.93
16 | 0.88 | 58 | 51.04 | 15.4 | 7.02 | 26.3513 | YES | 3.19
17 | 0.9 | 58 | 52.2 | 14.9 | 7 | 27.1088 | YES | 4.23
18 | 0.96 | 58 | 55.68 | 14.2 | 7.04 | 29.0319 | YES | 4.02
19 | 0.9 | 58 | 52.2 | 14.1 | 6.75 | 26.0608 | YES | 5.62
20 | 0.98 | 58 | 56.84 | 14 | 6.8 | 26.9745 | YES | 4.23
21 | 0.91 | 58 | 52.78 | 14.3 | 6.91 | 27.3224 | YES | 3.61
22 | 0.93 | 58 | 53.94 | 14.1 | 6.98 | 28.4851 | YES | 4.79
23 | 0.99 | 58 | 57.42 | 14 | 6.97 | 28.7663 | YES | 3.81
24 | 1.02 | 58 | 59.16 | 12.3 | 6.9 | 32.244 | YES | 4.23
25 | 1.01 | 58 | 58.58 | 12.6 | 6.88 | 30.6185 | YES | 4.79
26 | 1.03 | 58 | 59.74 | 12.4 | 6.96 | 32.7324 | YES | 3.05
27 | 1.06 | 58 | 61.48 | 12 | 6.9 | 33.0075 | YES | 4.72
28 | 1 | 58 | 58 | 12.1 | 6.98 | 33.4809 | YES | 4.3
29 | 1.02 | 58 | 59.16 | 12.4 | 6.96 | 32.6968 | YES | 3.95
30 | 1.07 | 58 | 62.06 | 12.6 | 6.91 | 31.1731 | YES | 4.02
31 | 1.1 | 58 | 63.8 | 12.5 | 6.86 | 30.9112 | YES | 5.07
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2