## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-11-24
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  |  | 0.13 | 0.12 |  | 0.13
2 |  | 0.11 | 0.12 | 0.1 |  |  | 0.12
3 |  |  |  | 0.09 | 0.09 | 0.07 | 0.09
4 |  | 0.07 | 0.07 | 0.07 |  |  | 0.07
5 | 0.06 | 0.06 | 0.07 | 0.06 |  |  | 0.07
6 |  |  |  |  | 0.11 | 0.12 | 0.12
7 |  | 0.08 | 0.08 | 0.08 |  |  | 0.08
8 |  |  | 0.06 | 0.07 | 0.07 |  | 0.07
9 |  | 0.07 | 0.07 | 0.06 |  |  | 0.07
10 | 0.08 | 0.08 |  |  | 0.09 | 0.07 | 0.09
11 |  |  | 0.11 | 0.1 |  |  | 0.11
12 |  | 0.14 | 0.14 | 0.11 |  |  | 0.14
13 |  | 0.13 | 0.14 | 0.11 |  |  | 0.14
14 | 0.1 | 0.09 | 0.08 | 0.08 |  |  | 0.1
15 |  |  | 0.15 | 0.14 |  |  | 0.15
16 |  |  | 0.11 | 0.14 | 0.14 |  | 0.14
17 |  | 0.1 | 0.08 | 0.09 |  |  | 0.1
18 | 0.15 | 0.12 | 0.12 |  |  |  | 0.15
19 |  |  |  | 0.16 | 0.15 | 0.16 | 0.16
20 |  |  | 0.09 | 0.08 | 0.09 |  | 0.09
21 |  |  | 0.13 | 0.14 | 0.13 |  | 0.14
22 |  | 0.14 | 0.12 | 0.14 |  |  | 0.14
23 |  |  |  | 0.13 | 0.13 | 0.1 | 0.13
24 |  |  |  | 0.12 | 0.11 | 0.1 | 0.12
25 |  |  | 0.08 | 0.09 |  |  | 0.09
26 | 0.08 | 0.1 | 0.07 |  |  |  | 0.1
27 |  | 0.08 |  | 0.08 | 0.07 | 0.07 | 0.08
28 |  |  | 0.05 | 0.06 |  |  | 0.06
29 |  | 0.05 |  | 0.06 | 0.07 | 0.05 | 0.07
30 |  | 0.07 | 0.06 | 0.06 |  |  | 0.07
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 12-09-24
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-11-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.03 | 58 | 59.74 | 12.3 | 7.01 | 33.5049 | YES | 4.4
2 | 1 | 58 | 58 | 13 | 6.84 | 29.3391 | YES | 3.2
3 | 1 | 58 | 58 | 13.2 | 6.77 | 28.2069 | YES | 5.01
4 | 0.96 | 58 | 55.68 | 13.6 | 7 | 29.7741 | YES | 4.4
5 | 0.9 | 58 | 52.2 | 13.8 | 6.96 | 28.7485 | YES | 4.99
6 | 0.93 | 58 | 53.94 | 13.7 | 6.91 | 28.5065 | YES | 4.86
7 | 0.91 | 58 | 52.78 | 13.4 | 6.84 | 28.2731 | YES | 4.42
8 | 0.88 | 58 | 51.04 | 13.1 | 6.98 | 30.2799 | YES | 5.87
9 | 1.02 | 58 | 59.16 | 12.7 | 6.92 | 30.9043 | YES | 3.33
10 | 0.99 | 58 | 57.42 | 12.2 | 6.94 | 32.7843 | YES | 5.18
11 | 1.06 | 58 | 61.48 | 12.2 | 6.91 | 32.7011 | YES | 4.92
12 | 1 | 58 | 58 | 11.9 | 6.73 | 31.1612 | YES | 4.25
13 | 1.04 | 58 | 60.32 | 11.5 | 6.8 | 32.8669 | YES | 4.63
14 | 0.96 | 58 | 55.68 | 11.7 | 6.73 | 31.4209 | YES | 4.79
15 | 1.02 | 58 | 59.16 | 11.2 | 6.85 | 34.001 | YES | 4.99
16 | 1.02 | 58 | 59.16 | 10.5 | 6.79 | 34.8388 | YES | 4.15
17 | 1.04 | 58 | 60.32 | 10.7 | 6.92 | 36.039 | YES | 4.62
18 | 0.95 | 58 | 55.1 | 11 | 6.71 | 32.5888 | YES | 4.37
19 | 0.94 | 58 | 54.52 | 11.2 | 6.77 | 32.802 | YES | 3.87
20 | 1.03 | 58 | 59.74 | 11.1 | 6.81 | 33.7931 | YES | 3.49
21 | 1.04 | 58 | 60.32 | 10.9 | 6.87 | 34.9744 | YES | 4.01
22 | 1 | 58 | 58 | 11.3 | 7.03 | 35.8484 | YES | 3.56
23 | 1.02 | 58 | 59.16 | 11.6 | 6.92 | 33.9424 | YES | 3.81
24 | 0.99 | 58 | 57.42 | 12.1 | 6.77 | 31.1534 | YES | 4.19
25 | 0.96 | 58 | 55.68 | 12.7 | 6.91 | 30.5802 | YES | 3.06
26 | 0.97 | 58 | 56.26 | 12.1 | 6.81 | 31.5072 | YES | 3.49
27 | 1.03 | 58 | 59.74 | 9.9 | 6.94 | 38.1723 | YES | 4.27
28 | 1.05 | 58 | 60.9 | 10.4 | 6.99 | 37.6821 | YES | 3.98
29 | 1.03 | 58 | 59.74 | 10.6 | 6.98 | 36.9875 | YES | 3.67
30 | 1.01 | 58 | 58.58 | 10.2 | 6.94 | 37.3543 | YES | 4.02
31 |  | 58
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2