## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-12-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.13 | 0.09 | 0.09 |  |  | 0.13
2 |  |  |  | 0.088 | 0.074 | 0.079 | 0.088
3 |  |  | 0.094 | 0.099 |  |  | 0.099
4 | 0.074 | 0.06 | 0.067 |  |  |  | 0.074
5 |  | 0.11 | 0.07 |  | 0.068 |  | 0.11
6 | 0.055 | 0.064 |  |  | 0.048 | 0.051 | 0.064
7 |  |  | 0.039 | 0.044 |  |  | 0.044
8 | 0.12 | 0.07 | 0.08 |  |  |  | 0.12
9 |  |  |  | 0.09 | 0.12 |  | 0.12
10 |  | 0.08 | 0.065 | 0.068 |  |  | 0.08
11 |  |  |  | 0.059 | 0.067 |  | 0.067
12 |  | 0.66 | 0.071 | 0.059 |  |  | 0.071
13 |  |  | 0.14 | 0.11 |  |  | 0.14
14 |  | 0.06 | 0.05 |  |  | 0.07 | 0.07
15 | 0.06 |  |  | 0.07 | 0.07 |  | 0.07
16 |  |  | 0.04 | 0.06 |  |  | 0.06
17 |  | 0.07 | 0.07 |  |  |  | 0.07
18 |  |  |  | 0.09 | 0.08 |  | 0.09
19 |  | 0.051 | 0.06 | 0.04 |  |  | 0.06
20 | 0.08 | 0.07 |  |  |  | 0.06 | 0.08
21 | 0.06 |  |  |  | 0.09 | 0.12 | 0.12
22 |  |  |  | 0.05 | 0.07 |  | 0.07
23 |  | 0.08 | 0.06 | 0.04 |  |  | 0.08
24 |  | 0.11 | 0.14 | 0.09 |  |  | 0.11
25 |  |  |  | 0.08 | 0.08 |  | 0.08
26 |  | 0.07 | 0.05 |  |  | 0.06 | 0.07
27 | 0.08 |  |  |  | 0.09 | 0.1 | 0.1
28 |  |  | 0.07 | 0.07 | 0.07 |  | 0.07
29 |  | 0.04 | 0.06 |  |  |  | 0.06
30 | 0.05 | 0.07 |  |  | 0.06 | 0.06 | 0.07
31 |  |  | 0.05 | 0.05 |  |  | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 01/09/2025
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2024-12-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 58 | 57.42 | 13.9 | 6.95 | 28.745 | YES | 5.06
2 | 1.03 | 58 | 59.74 | 13.3 | 6.97 | 30.2811 | YES | 5.55
3 | 1.04 | 58 | 60.32 | 13.6 | 7 | 30.0469 | YES | 4.92
4 | 0.98 | 58 | 56.84 | 13.4 | 6.88 | 28.9264 | YES | 4.95
5 | 0.87 | 58 | 50.46 | 13.8 | 6.87 | 27.7083 | YES | 5.02
6 | 0.96 | 58 | 55.68 | 13.5 | 6.91 | 28.9893 | YES | 4.49
7 | 1.05 | 58 | 60.9 | 13.9 | 6.82 | 27.5782 | YES | 4.98
8 | 1 | 58 | 58 | 12.6 | 6.83 | 30.0219 | YES | 5.69
9 | 0.97 | 58 | 56.26 | 12.8 | 6.88 | 30.075 | YES | 6.03
10 | 0.99 | 58 | 57.42 | 12.6 | 6.77 | 29.3277 | YES | 4.98
11 | 1.02 | 58 | 59.16 | 13.1 | 6.68 | 27.5252 | YES | 5.03
12 | 1.04 | 58 | 60.32 | 13.3 | 6.82 | 28.6747 | YES | 5.55
13 | 1.06 | 58 | 61.48 | 13.1 | 6.99 | 31.0222 | YES | 5.55
14 | 0.98 | 58 | 56.84 | 12.9 | 6.74 | 28.3947 | YES | 5.69
15 | 1.02 | 58 | 59.16 | 13.5 | 6.93 | 29.4059 | YES | 6.25
16 | 1.05 | 58 | 60.9 | 13.7 | 6.98 | 29.6602 | YES | 4.68
17 | 0.97 | 58 | 56.26 | 12.9 | 6.76 | 28.5737 | YES | 5.94
18 | 0.96 | 58 | 55.68 | 13.1 | 6.88 | 29.4449 | YES | 5.93
19 | 1.04 | 58 | 60.32 | 13.4 | 6.92 | 29.5607 | YES | 5.59
20 | 1 | 58 | 58 | 13.3 | 6.79 | 28.2278 | YES | 6.02
21 | 0.98 | 58 | 56.84 | 12.9 | 6.86 | 29.6879 | YES | 6.19
22 | 0.96 | 58 | 55.68 | 13.6 | 6.94 | 29.1186 | YES | 5.79
23 | 0.99 | 58 | 57.42 | 13.1 | 7.01 | 31.0047 | YES | 4.98
24 | 1.04 | 58 | 60.32 | 12.8 | 6.93 | 30.883 | YES | 4.43
25 | 1.06 | 58 | 61.48 | 12.6 | 6.98 | 31.9554 | YES | 6.15
26 | 1.02 | 58 | 59.16 | 13.3 | 6.85 | 28.9297 | YES | 5.54
27 | 1.07 | 58 | 62.06 | 13.1 | 6.92 | 30.2622 | YES | 6.76
28 | 1.03 | 58 | 59.74 | 13.2 | 6.89 | 29.5929 | YES | 6.39
29 | 1.05 | 58 | 60.9 | 12.9 | 6.87 | 30.037 | YES | 4.67
30 | 1.04 | 58 | 60.32 | 13.1 | 6.84 | 29.2771 | YES | 5.03
31 | 1.02 | 58 | 59.16 | 12.7 | 6.89 | 30.5626 | YES | 4.69
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2