## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-01-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.07 | 0.07 | 0.09 |  |  | 0.09
2 | 0.04 | 0.05 |  |  | 0.06 |  | 0.06
3 |  | 0.07 | 0.05 |  |  | 0.06 | 0.07
4 | 0.05 | 0.05 |  |  | 0.08 | 0.05 | 0.08
5 |  |  | 0.05 | 0.05 | 0.04 |  | 0.05
6 |  |  | 0.06 | 0.06 | 0.04 |  | 0.06
7 | 0.04 | 0.05 |  |  | 0.06 | 0.05 | 0.06
8 |  |  | 0.04 | 0.05 |  |  | 0.05
9 | 0.06 | 0.04 |  | 0.05 | 0.05 |  | 0.06
10 |  |  | 0.07 | 0.05 |  | 0.06 | 0.07
11 |  |  | 0.09 | 0.08 |  |  | 0.09
12 | 0.07 | 0.07 |  |  | 0.08 | 0.06 | 0.08
13 |  |  | 0.07 | 0.08 | 0.05 |  | 0.08
14 |  |  | 0.09 | 0.07 | 0.08 |  | 0.09
15 | 0.05 | 0.06 | 0.05 |  |  |  | 0.06
16 |  |  | 0.07 | 0.08 |  |  | 0.08
17 | 0.06 | 0.06 |  |  | 0.07 | 0.09 | 0.09
18 |  |  | 0.05 | 0.05 | 0.07 |  | 0.07
19 |  |  |  | 0.09 | 0.08 | 0.09 | 0.09
20 |  |  | 0.07 | 0.05 | 0.06 |  | 0.07
21 |  | 0.04 | 0.05 | 0.07 |  |  | 0.07
22 |  | 0.04 | 0.04 |  |  |  | 0.04
23 | 0.06 | 0.06 |  |  | 0.08 | 0.08 | 0.08
24 |  |  | 0.05 | 0.05 |  |  | 0.05
25 |  | 0.07 | 0.07 |  |  |  | 0.07
26 | 0.05 | 0.04 | 0.05 |  |  |  | 0.05
27 |  |  | 0.05 | 0.06 |  |  | 0.06
28 | 0.04 | 0.04 |  |  | 0.07 |  | 0.07
29 |  | 0.05 |  | 0.06 | 0.06 |  | 0.06
30 |  | 0.08 | 0.09 |  |  |  | 0.09
31 | 0.07 | 0.05 |  |  | 0.05 |  | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 02-09-25
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.06 | 58 | 61.48 | 12.4 | 7.02 | 33.5148 | YES | 4.9
2 | 0.98 | 58 | 56.84 | 12.5 | 7.08 | 33.0793 | YES | 5.03
3 | 0.99 | 58 | 57.42 | 12.7 | 7.09 | 32.7998 | YES | 4.78
4 | 1.02 | 58 | 59.16 | 12.8 | 6.9 | 30.472 | YES | 3.06
5 | 1 | 58 | 58 | 11.9 | 6.94 | 33.4528 | YES | 4.05
6 | 0.97 | 58 | 56.26 | 12 | 6.99 | 33.6993 | YES | 4.9
7 | 1.02 | 58 | 59.16 | 12.1 | 6.77 | 31.2545 | YES | 4.07
8 | 1.01 | 58 | 58.58 | 11.8 | 6.98 | 34.1658 | YES | 3.98
9 | 0.95 | 58 | 55.1 | 12.2 | 6.85 | 31.6647 | YES | 5.02
10 | 1.01 | 58 | 58.58 | 11.4 | 6.88 | 33.8769 | YES | 4.18
11 | 0.98 | 58 | 56.84 | 10.7 | 6.99 | 36.6726 | YES | 4.27
12 | 1.02 | 58 | 59.16 | 9.9 | 7.03 | 39.3375 | YES | 3.98
13 | 1.04 | 58 | 60.32 | 11.1 | 6.94 | 35.365 | YES | 4.22
14 | 1.05 | 58 | 60.9 | 11.5 | 6.9 | 34.0397 | YES | 4.19
15 | 1.01 | 58 | 58.58 | 11.9 | 6.82 | 32.1553 | YES | 4.12
16 | 0.97 | 58 | 56.26 | 10.9 | 6.8 | 33.8881 | YES | 4.14
17 | 1 | 58 | 58 | 11 | 6.85 | 34.3633 | YES | 4.33
18 | 1.01 | 58 | 58.58 | 11.2 | 6.79 | 33.2781 | YES | 4.18
19 | 1.06 | 58 | 61.48 | 11.6 | 7 | 35.035 | YES | 3.97
20 | 0.95 | 58 | 55.1 | 11.5 | 6.93 | 34.015 | YES | 3.62
21 | 1.02 | 58 | 59.16 | 11.5 | 6.88 | 33.6981 | YES | 4.12
22 | 1.03 | 58 | 59.74 | 11 | 7.07 | 37.1783 | YES | 3.99
23 | 1 | 58 | 58 | 11.2 | 6.78 | 33.1292 | YES | 4.04
24 | 1.05 | 58 | 60.9 | 11.8 | 6.89 | 33.281 | YES | 3.77
25 | 0.97 | 58 | 56.26 | 11.4 | 6.93 | 34.3083 | YES | 4.09
26 | 1.03 | 58 | 59.74 | 11 | 6.99 | 36.169 | YES | 4.17
27 | 1.03 | 58 | 59.74 | 11.4 | 7.03 | 35.7364 | YES | 5
28 | 0.96 | 58 | 55.68 | 10.9 | 6.78 | 33.6216 | YES | 4.76
29 | 1.02 | 58 | 59.16 | 11.1 | 6.81 | 33.7562 | YES | 4.32
30 | 0.99 | 58 | 57.42 | 10.8 | 6.93 | 35.7332 | YES | 4.12
31 | 1.03 | 58 | 59.74 | 11.7 | 6.99 | 34.5783 | YES | 4.18
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2