## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-04-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.08 | 0.06 |  |  | 0.07 | 0.07 | 0.08
2 |  |  | 0.06 | 0.06 | 0.05 |  | 0.06
3 |  | 0.07 | 0.05 |  |  |  | 0.07
4 | 0.07 | 0.08 | 0.05 |  |  |  | 0.08
5 |  |  | 0.07 | 0.07 | 0.06 |  | 0.07
6 |  | 0.06 | 0.05 | 0.06 |  |  | 0.06
7 |  |  | 0.07 | 0.05 |  | 0.06 | 0.07
8 | 0.08 |  |  | 0.07 | 0.07 |  | 0.08
9 |  | 0.05 | 0.06 |  |  | 0.07 | 0.07
10 | 0.05 |  |  | 0.06 | 0.06 |  | 0.06
11 |  |  | 0.07 | 0.06 | 0.07 |  | 0.07
12 |  | 0.05 | 0.03 |  |  |  | 0.05
13 | 0.06 | 0.06 |  |  |  | 0.05 | 0.06
14 | 0.07 |  | 0.08 | 0.05 |  |  | 0.08
15 |  | 0.06 | 0.05 |  |  | 0.05 | 0.06
16 | 0.04 |  |  | 0.05 | 0.05 |  | 0.05
17 |  | 0.07 | 0.05 |  |  | 0.07 | 0.07
18 | 0.07 |  |  | 0.04 | 0.04 |  | 0.07
19 |  |  | 0.06 | 0.06 |  |  | 0.06
20 |  | 0.07 | 0.05 |  |  | 0.05 | 0.07
21 | 0.04 |  |  | 0.06 | 0.05 |  | 0.06
22 |  | 0.05 | 0.07 |  |  |  | 0.07
23 | 0.06 | 0.05 |  |  |  | 0.03 | 0.06
24 | 0.04 |  |  | 0.05 |  |  | 0.05
25 |  | 0.05 | 0.06 |  |  |  | 0.06
26 | 0.04 | 0.04 |  |  | 0.03 | 0.04 | 0.04
27 |  |  | 0.05 | 0.05 |  |  | 0.05
28 |  | 0.06 | 0.04 |  |  | 0.05 | 0.06
29 | 0.04 |  |  | 0.04 | 0.06 |  | 0.06
30 |  |  | 0.05 | 0.05 |  |  | 0.05
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 5-9-25
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.05 | 58 | 60.9 | 10.9 | 6.74 | 33.4952 | YES | 4.44
2 | 0.98 | 58 | 56.84 | 11.2 | 6.68 | 31.9575 | YES | 4.44
3 | 0.81 | 58 | 46.98 | 10.1 | 6.83 | 35.4105 | YES | 4.71
4 | 0.96 | 58 | 55.68 | 10.4 | 6.63 | 32.9865 | YES | 4.37
5 | 1.03 | 58 | 59.74 | 11.6 | 6.59 | 30.3966 | YES | 4.09
6 | 1 | 58 | 58 | 11.4 | 6.96 | 34.7755 | YES | 3.88
7 | 0.99 | 58 | 57.42 | 11.6 | 6.84 | 32.9245 | YES | 3.61
8 | 0.96 | 58 | 55.68 | 12.1 | 6.76 | 30.9485 | YES | 4.37
9 | 1.05 | 58 | 60.9 | 11.8 | 6.78 | 32.0645 | YES | 3.47
10 | 1.02 | 58 | 59.16 | 11.5 | 6.88 | 33.6981 | YES | 4.16
11 | 0.95 | 58 | 55.1 | 11.3 | 6.65 | 31.3348 | YES | 3.81
12 | 0.99 | 58 | 57.42 | 11.4 | 6.86 | 33.5737 | YES | 3.61
13 | 1.04 | 58 | 60.32 | 12.1 | 6.88 | 32.5062 | YES | 3.61
14 | 1.02 | 58 | 59.16 | 11.9 | 6.72 | 31.1238 | YES | 3.81
15 | 0.88 | 58 | 51.04 | 12.2 | 6.75 | 30.3885 | YES | 4.23
16 | 0.92 | 58 | 53.36 | 11.9 | 6.72 | 30.7898 | YES | 4.02
17 | 0.96 | 58 | 55.68 | 11.9 | 6.66 | 30.3073 | YES | 7.08
18 | 1.05 | 58 | 60.9 | 11.2 | 6.65 | 31.8767 | YES | 4.09
19 | 0.98 | 58 | 56.84 | 11.6 | 6.58 | 30.1327 | YES | 3.88
20 | 0.91 | 58 | 52.78 | 11.8 | 6.88 | 32.6664 | YES | 4.16
21 | 0.99 | 58 | 57.42 | 12.1 | 6.92 | 32.7706 | YES | 5.48
22 | 0.87 | 58 | 50.46 | 12.4 | 6.94 | 31.9517 | YES | 3.81
23 | 1.04 | 58 | 60.32 | 11.8 | 6.96 | 34.0454 | YES | 4.26
24 | 1 | 58 | 58 | 11.4 | 6.89 | 33.9552 | YES | 2.7
25 | 1.06 | 58 | 61.48 | 11.6 | 6.92 | 34.0913 | YES | 3.81
26 | 0.95 | 58 | 55.1 | 11.3 | 6.99 | 35.1665 | YES | 3.47
27 | 0.99 | 58 | 57.42 | 12.1 | 6.8 | 31.4693 | YES | 4.09
28 | 0.96 | 58 | 55.68 | 11.9 | 6.83 | 32.0895 | YES | 5.6
29 | 0.94 | 58 | 54.52 | 11.6 | 6.86 | 32.9684 | YES | 4.17
30 | 1.02 | 58 | 59.16 | 11.8 | 6.56 | 29.6865 | YES | 3.38
31 |  | 58
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2