## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-07-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.055 | 0.079 |  |  | 0.079
2 | 0.045 | 0.053 |  |  |  |  | 0.053
3 |  |  | 0.077 | 0.69 |  |  | 0.077
4 |  | 0.063 | 0.059 |  | 0.061 |  | 0.063
5 |  |  |  | 0.059 | 0.047 | 0.049 | 0.059
6 |  | 0.054 | 0.061 |  |  |  | 0.061
7 |  |  |  | 0.057 | 0.062 | 0.068 | 0.068
8 |  |  | 0.061 | 0.049 |  |  | 0.061
9 |  |  | 0.058 | 0.054 |  |  | 0.058
10 |  |  |  |  | 0.067 | 0.057 | 0.067
11 |  |  |  | 0.059 | 0.046 |  | 0.059
12 |  | 0.061 | 0.067 |  |  |  | 0.067
13 |  |  |  |  | 0.051 | 0.055 | 0.055
14 |  |  | 0.059 | 0.061 | 0.065 |  | 0.065
15 |  |  |  | 0.052 | 0.057 |  | 0.057
16 | 0.055 | 0.055 | 0.063 |  |  |  | 0.063
17 |  |  | 0.052 | 0.057 | 0.051 |  | 0.057
18 |  |  |  |  | 0.053 | 0.062 | 0.062
19 | 0.048 |  |  |  |  | 0.054 | 0.054
20 |  |  | 0.064 | 0.046 |  |  | 0.064
21 |  | 0.059 | 0.045 | 0.059 |  |  | 0.059
22 |  |  |  |  | 0.05 | 0.048 | 0.05
23 |  |  | 0.048 | 0.044 | 0.053 |  | 0.053
24 |  |  | 0.066 |  |  | 0.062 | 0.066
25 | 0.07 |  | 0.064 | 0.059 |  |  | 0.07
26 |  |  |  | 0.056 | 0.056 | 0.057 | 0.056
27 |  | 0.072 | 0.071 | 0.059 |  |  | 0.072
28 |  |  | 0.056 | 0.054 |  |  | 0.056
29 | 0.06 |  |  | 0.058 | 0.065 |  | 0.065
30 |  |  | 0.069 | 0.061 |  |  | 0.069
31 |  |  | 0.068 | 0.061 |  |  | 0.068
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 08/09/2025
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226 D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.05 | 58 | 60.9 | 15.3 | 6.98 | 26.6499 | YES | 20
2 | 1 | 58 | 58 | 15 | 6.87 | 25.9514 | YES | 20
3 | 1.04 | 58 | 60.32 | 14.9 | 6.68 | 24.4519 | YES | 20
4 | 0.94 | 58 | 54.52 | 15.3 | 6.76 | 24.245 | YES | 20
5 | 0.99 | 58 | 57.42 | 15.2 | 6.78 | 24.7326 | YES | 20
6 | 1 | 58 | 58 | 15.6 | 6.89 | 25.1141 | YES | 20
7 | 0.97 | 58 | 56.26 | 16 | 6.68 | 22.5262 | YES | 20
8 | 0.89 | 58 | 51.62 | 15.8 | 6.73 | 23.0495 | YES | 20
9 | 1.04 | 58 | 60.32 | 15.4 | 6.82 | 24.9119 | YES | 20
10 | 1.03 | 58 | 59.74 | 15.9 | 6.77 | 23.6165 | YES | 20
11 | 1.08 | 58 | 62.64 | 16.6 | 6.99 | 24.6001 | YES | 20
12 | 0.95 | 58 | 55.1 | 16.1 | 6.75 | 22.9157 | YES | 20
13 | 0.87 | 58 | 50.46 | 16.2 | 6.69 | 22.0528 | YES | 20
14 | 1.02 | 58 | 59.16 | 15.4 | 6.94 | 25.9913 | YES | 20
15 | 1.05 | 58 | 60.9 | 15.9 | 6.96 | 25.4093 | YES | 20
16 | 0.99 | 58 | 57.42 | 15.1 | 7.02 | 27.2266 | YES | 20
17 | 1.04 | 58 | 60.32 | 15.5 | 7.05 | 26.9581 | YES | 20
18 | 1.06 | 58 | 61.48 | 15.5 | 6.77 | 24.3437 | YES | 20
19 | 1.02 | 58 | 59.16 | 15.3 | 6.81 | 24.9291 | YES | 20
20 | 1.05 | 58 | 60.9 | 15.6 | 6.76 | 24.063 | YES | 20
21 | 0.92 | 58 | 53.36 | 15.3 | 6.74 | 24.0096 | YES | 20
22 | 0.94 | 58 | 54.52 | 15.4 | 7.06 | 26.9306 | YES | 20
23 | 0.94 | 58 | 54.52 | 15.6 | 6.62 | 22.5498 | YES | 20
24 | 0.99 | 58 | 57.42 | 15.9 | 7 | 25.6141 | YES | 20
25 | 1 | 58 | 58 | 15.6 | 6.79 | 24.1947 | YES | 20
26 | 1.02 | 58 | 59.16 | 15.3 | 6.88 | 25.588 | YES | 20
27 | 0.94 | 58 | 54.52 | 15.9 | 6.82 | 23.8142 | YES | 20
28 | 0.9 | 58 | 52.2 | 15.8 | 6.77 | 23.4235 | YES | 20
29 | 0.85 | 58 | 49.3 | 15.4 | 7.03 | 26.3589 | YES | 20
30 | 1.05 | 58 | 60.9 | 15.9 | 6.74 | 23.407 | YES | 20
31 | 1.04 | 58 | 60.32 | 16.2 | 6.81 | 23.5202 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2