## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-08-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.065 | 0.051 |  |  | 0.065
2 | 0.039 | 0.048 | 0.054 |  |  |  | 0.054
3 |  |  | 0.049 | 0.043 |  |  | 0.049
4 | 0.052 | 0.053 |  |  |  | 0.05 | 0.053
5 | 0.048 |  |  | 0.051 | 0.046 |  | 0.051
6 |  | 0.049 | 0.046 | 0.046 |  |  | 0.049
7 |  |  |  | 0.062 | 0.054 | 0.045 | 0.062
8 |  | 0.049 | 0.047 | 0.055 |  |  | 0.055
9 | 0.057 | 0.055 | 0.046 |  |  |  | 0.057
10 |  |  | 0.047 | 0.046 | 0.044 |  | 0.047
11 |  | 0.052 | 0.05 | 0.046 |  |  | 0.052
12 |  |  | 0.046 | 0.049 |  | 0.036 | 0.046
13 |  | 0.039 | 0.041 | 0.049 |  |  | 0.049
14 |  | 0.041 | 0.046 | 0.043 |  |  | 0.046
15 |  |  |  | 0.056 | 0.052 |  | 0.056
16 |  | 0.053 | 0.049 |  | 0.051 |  | 0.053
17 |  |  | 0.045 | 0.036 |  |  | 0.045
18 |  | 0.062 | 0.057 | 0.05 |  |  | 0.062
19 |  |  |  | 0.049 | 0.041 | 0.048 | 0.049
20 |  | 0.065 | 0.064 | 0.061 |  |  | 0.065
21 |  |  |  | 0.055 | 0.059 |  | 0.059
22 |  | 0.053 | 0.058 |  |  |  | 0.058
23 | 0.042 | 0.041 |  |  |  | 0.049 | 0.049
24 |  |  | 0.048 | 0.046 |  |  | 0.048
25 |  | 0.045 | 0.047 |  |  |  | 0.047
26 | 0.039 |  |  | 0.049 | 0.044 |  | 0.049
27 |  | 0.053 |  |  | 0.049 |  | 0.053
28 |  |  |  | 0.045 | 0.053 |  | 0.053
29 | 0.049 |  |  | 0.044 |  |  | 0.049
30 | 0.056 |  | 0.049 | 0.041 |  |  | 0.056
31 |  | 0.04 | 0.037 |  |  | 0.046 | 0.046
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 09-09-25
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.93 | 58 | 53.94 | 17.5 | 6.87 | 21.7606 | YES | 20
2 | 0.85 | 58 | 49.3 | 17.2 | 6.86 | 21.9194 | YES | 20
3 | 0.82 | 58 | 47.56 | 17.5 | 6.9 | 21.7294 | YES | 20
4 | 0.91 | 58 | 52.78 | 16.9 | 6.85 | 22.4379 | YES | 20
5 | 0.87 | 58 | 50.46 | 16.5 | 6.79 | 22.4356 | YES | 20
6 | 0.84 | 58 | 48.72 | 17 | 6.84 | 22.0258 | YES | 20
7 | 0.98 | 58 | 56.84 | 17.4 | 6.88 | 22.1169 | YES | 20
8 | 1.06 | 58 | 61.48 | 17.6 | 6.83 | 21.6141 | YES | 20
9 | 1.03 | 58 | 59.74 | 17.5 | 6.77 | 21.2032 | YES | 20
10 | 0.89 | 58 | 51.62 | 17.7 | 6.79 | 20.7387 | YES | 20
11 | 0.88 | 58 | 51.04 | 18 | 6.84 | 20.6836 | YES | 20
12 | 0.83 | 58 | 48.14 | 18.2 | 6.81 | 20.0611 | YES | 20
13 | 0.89 | 58 | 51.62 | 17.3 | 6.89 | 22.1197 | YES | 20
14 | 0.9 | 58 | 52.2 | 17.6 | 6.73 | 20.4379 | YES | 20
15 | 0.94 | 58 | 54.52 | 18.1 | 6.8 | 20.3787 | YES | 20
16 | 0.96 | 58 | 55.68 | 17.8 | 6.71 | 20.1517 | YES | 20
17 | 1.02 | 58 | 59.16 | 18 | 6.76 | 20.3987 | YES | 20
18 | 1.06 | 58 | 61.48 | 17.6 | 6.81 | 21.4527 | YES | 20
19 | 0.98 | 58 | 56.84 | 17.5 | 6.88 | 21.9683 | YES | 20
20 | 0.95 | 58 | 55.1 | 18.1 | 6.92 | 21.3416 | YES | 20
21 | 0.99 | 58 | 57.42 | 17.9 | 6.83 | 21.0107 | YES | 20
22 | 0.96 | 58 | 55.68 | 17.7 | 6.74 | 20.5182 | YES | 20
23 | 1 | 58 | 58 | 18.1 | 6.88 | 21.1455 | YES | 20
24 | 0.97 | 58 | 56.26 | 17.6 | 6.89 | 21.8774 | YES | 20
25 | 0.93 | 58 | 53.94 | 17.7 | 6.94 | 22.0393 | YES | 20
26 | 0.96 | 58 | 55.68 | 18 | 6.79 | 20.4873 | YES | 20
27 | 0.95 | 58 | 55.1 | 18.3 | 6.7 | 19.3856 | YES | 20
28 | 0.89 | 58 | 51.62 | 18.1 | 6.75 | 19.8844 | YES | 20
29 | 0.86 | 58 | 49.88 | 18 | 6.79 | 20.2521 | YES | 20
30 | 0.91 | 58 | 52.78 | 17.9 | 6.88 | 21.2117 | YES | 20
31 | 1 | 58 | 58 | 18.3 | 6.79 | 20.1689 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2