## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-09-01
System Name: | Rainbow Rock Village MHP |  |  | ID#: 41 01062 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.075 | 0.068 | 0.071 |  |  | 0.075
2 |  | 0.049 | 0.056 |  | 0.063 |  | 0.063
3 |  | 0.07 | 0.05 |  |  | 0.06 | 0.07
4 | 0.055 |  |  | 0.063 | 0.068 |  | 0.068
5 |  |  | 0.055 | 0.049 |  |  | 0.055
6 | 0.062 | 0.065 |  |  | 0.055 | 0.069 | 0.069
7 |  |  | 0.067 | 0.064 |  |  | 0.067
8 |  | 0.068 | 0.068 |  |  | 0.059 | 0.068
9 | 0.059 |  |  | 0.061 | 0.059 |  | 0.061
10 |  |  | 0.073 | 0.07 |  |  | 0.073
11 | 0.063 | 0.054 |  |  | 0.063 |  | 0.063
12 |  |  | 0.059 | 0.052 | 0.064 |  | 0.064
13 |  | 0.044 | 0.053 | 0.051 |  |  | 0.053
14 |  |  | 0.071 | 0.075 |  |  | 0.075
15 |  | 0.066 | 0.063 |  |  | 0.059 | 0.066
16 |  | 0.056 | 0.06 |  | 0.063 |  | 0.063
17 |  | 0.052 | 0.059 |  |  | 0.065 | 0.065
18 | 0.053 |  |  | 0.049 |  |  | 0.053
19 |  | 0.039 | 0.046 |  |  | 0.054 | 0.054
20 |  |  |  | 0.069 | 0.073 |  | 0.073
21 |  | 0.061 | 0.059 |  |  |  | 0.061
22 | 0.044 | 0.049 |  |  | 0.062 |  | 0.062
23 |  |  | 0.077 | 0.081 |  |  | 0.081
24 |  | 0.069 | 0.076 |  |  | 0.062 | 0.076
25 |  |  |  | 0.066 | 0.057 |  | 0.066
26 |  | 0.059 |  | 0.065 |  |  | 0.065
27 |  |  | 0.058 | 0.066 |  |  | 0.066
28 |  | 0.054 |  |  | 0.068 |  | 0.068
29 |  |  | 0.049 | 0.051 |  |  | 0.051
30 |  | 0.063 | 0.061 |  |  | 0.054 | 0.061
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Brenda L Vasquez
[5 empty] | SIGNATURE: Brenda L Vasquez |  |  | DATE: 10-09-25
[5 empty] | PHONE #: (541) 254-1909 |  |  | CERT #:T070226-D070226
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Rainbow Rock Village MHP |  | ID#: 41 01062 |  | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.86 | 58 | 49.88 | 16.2 | 7.03 | 25.0106 | YES | 20
2 | 1.02 | 58 | 59.16 | 16.5 | 6.9 | 23.7837 | YES | 20
3 | 0.94 | 58 | 54.52 | 17 | 6.85 | 22.3643 | YES | 20
4 | 0.96 | 58 | 55.68 | 16.8 | 6.98 | 23.8507 | YES | 20
5 | 1 | 58 | 58 | 16.4 | 6.91 | 23.9785 | YES | 20
6 | 1.03 | 58 | 59.74 | 16.9 | 6.96 | 23.7044 | YES | 20
7 | 0.9 | 58 | 52.2 | 16.5 | 7.01 | 24.4415 | YES | 20
8 | 0.89 | 58 | 51.62 | 15.9 | 7 | 25.3224 | YES | 20
9 | 0.96 | 58 | 55.68 | 16.6 | 6.85 | 23.0278 | YES | 20
10 | 1.06 | 58 | 61.48 | 16.9 | 6.96 | 23.7861 | YES | 20
11 | 1.04 | 58 | 60.32 | 17.2 | 6.91 | 22.8269 | YES | 20
12 | 0.87 | 58 | 50.46 | 16.8 | 6.96 | 23.4298 | YES | 20
13 | 1.01 | 58 | 58.58 | 16.6 | 7.01 | 24.5862 | YES | 20
14 | 0.99 | 58 | 57.42 | 15.9 | 6.85 | 24.221 | YES | 20
15 | 1.04 | 58 | 60.32 | 16.3 | 6.91 | 24.2513 | YES | 20
16 | 0.95 | 58 | 55.1 | 16.9 | 6.99 | 23.7522 | YES | 20
17 | 0.99 | 58 | 57.42 | 17.3 | 6.95 | 22.8835 | YES | 20
18 | 1 | 58 | 58 | 16.9 | 6.88 | 22.9271 | YES | 20
19 | 1.03 | 58 | 59.74 | 16.9 | 6.94 | 23.528 | YES | 20
20 | 0.95 | 58 | 55.1 | 17.2 | 6.9 | 22.5075 | YES | 20
21 | 0.97 | 58 | 56.26 | 17.6 | 6.86 | 21.6329 | YES | 20
22 | 1.04 | 58 | 60.32 | 16.5 | 7.02 | 24.9299 | YES | 20
23 | 1.06 | 58 | 61.48 | 16.8 | 7.04 | 24.6722 | YES | 20
24 | 0.98 | 58 | 56.84 | 16.4 | 6.99 | 24.6485 | YES | 20
25 | 0.96 | 58 | 55.68 | 17.2 | 7.04 | 23.7439 | YES | 20
26 | 0.91 | 58 | 52.78 | 17.4 | 6.95 | 22.5218 | YES | 20
27 | 0.94 | 58 | 54.52 | 16.7 | 6.98 | 23.9565 | YES | 20
28 | 1.01 | 58 | 58.58 | 16.6 | 6.9 | 23.5972 | YES | 20
29 | 0.96 | 58 | 55.68 | 16.9 | 6.87 | 22.7368 | YES | 20
30 | 0.94 | 58 | 54.52 | 17.4 | 6.95 | 22.5996 | YES | 20
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2